## AC controller
Project: | Energy saving - AC controller
Project Owner: | Mr.swapnil Sali
Potential Saving in Rs Thousand: |  | Estimated Expense in Rs Thousand: | 34290 | Net Saving in FY16-17 in Rs Thousand:
Base Data:
Sample calculation as shown below
AC TR capacity | Saver off kwh | saver on kwh | Difference in kwh | % saving achieved | operating hrs. | Rs saved
1.5 | 3.3 | 2.3 | 1 | 30.303 | 24 | 3600
1.5 | 2.2 | 1.47 | 0.73 | 33.1818 | 24 | 2628
5.5 | 3.3 | 3 | 0.3 | 9.0909 | 24 | 1080
5.5 | 3.558 | 2.662 | 0.896 | 25.1827 | 24 | 3225.6
11 | 10.15 | 6.27 | 3.88 | 38.2266 | 24 | 13968
8.75 | 8 | 4.32 | 3.68 | 46 | 24 | 13248
11 | 2.79 | 0.42 | 2.37 | 84.9462 | #REF! | #REF!
11 | 8.17 | 6.08 | 2.09 | 25.5814 | #REF! | #REF!
11 | 3.2 | 1.47 | 1.73 | 54.0625 | #REF! | #REF!
11 | 7.2 | 6.3 | 0.9 | 12.5 | #REF! | #REF!
| July | August | September | October | November | December | January | February | March | Total till date
Saving achieved in Rs thousand | 10173 | 22292 | 74109 | 76580 | 74109 | 51970 | 99268 | 86846 | 96151 | 591498
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das
Note on J22: 3 new controller installed

## 2. Power saving_Water pumps (hidden)
Project: | Power saving in water pumps
Project Owner: | Aniruddha Bansod
Potential Saving in Rs Lac: | 15 | Estimated Expense in Rs Lac: | 0.5 | Net Saving in FY15-16 in Rs Lac: | 14.5
Base Data:
Water pumps detail collected by team
Total app Power of water pumps |  |  |  | 2800 | KW | to be revised
Assuming 50% in operation, operating load |  |  |  | 1400 | KWH
Estimated power cost |  |  |  | 7.5 | Rs/KWH
Estimated power saving of 5% on account of efficiency / optimization |  |  |  | 70 | KWH
Total saving @ 330 working days |  |  |  | 4158000 | Rs/Yr
| July | August | September | October | November | December | January | February | March
Saving achieved in Lac
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das
Status till date: 19.10.15
Water Pump more than 45 KW selected under project
For improvement due to network flow optimization, individual circuit being studied proper action being taken
For pump efficiency inprovement, flow measurement PO to be released - Expected by 24.10.15

## Sheet1
|  |  | Reading Sheet | [5 empty] | operating days
Inst date | Date | operating hrs | AC location | TR | Saver off kwh | saver on kwh | Difference in kwh | % saving achieved | 2017-04-01 | Rs saved | Investment | condition | monthly saving
2016-06-04 | 2016-06-04 | 24 | substation window | 1.5 | 3.3 | 2.3 | 1 | 30.303 | 301 | 43777.44 |  | removed conroller feb 17
2016-07-14 | 2016-07-29 | 24 | phase 1 split AC | 5.5 | 3.558 | 2.662 | 0.896 | 25.1827 | 261 | 34012.0166 | 5715 |  | 4039.7414
2016-08-11 | 2016-08-11 | 24 | Linde ductable Ac | 8.75 | 8 | 4.32 | 3.68 | 46 | 233 | 124706.0736 | 5715 |  | 16591.7952
2016-08-19 | 2016-08-19 | 24 | perroni package AC-1 | 11 | 2.79 | 0.42 | 2.37 | 84.9462 | 225 | 77555.88 | 5715 | both package AC run | 10685.4768
2016-08-11 | 2016-08-24 | 24 | perroni package AC-2 | 11 | 7.2 | 6.3 | 0.9 | 12.5 | 233 | 30498.768 |  | removed conroller feb 17
2016-09-02 | 2016-09-02 | 24 | admin cold storage 1st flr unit-1 | 8.75 | 5.97 | 2.96 | 3.01 | 50.4188 | 211 | 92370.3984 |  | only one running out of 3
2017-02-01 | 2017-02-01 | 24 | admin cold storage 1st flr | 8.75 | 2.6 | 1.9 | 0.7 | 26.9231 | 59 | 6006.672 | 5715 | all 3 are running | 3156.048
2016-12-09 | 2016-12-12 | 12 | 2nd flr office ,near lift | 11 | 5.15 | 2.3 | 2.85 | 55.3398 | 113 | 23419.476
2017-01-10 | 1 day calculation | 1 | 2ND FLOOR OFFICE AC |  | 200 | 170 | 30 | 15 | 81 | 14725.8 | 22860 |  | 5635.8
2017-01-18 |  | 24 | GLC lab | 5.5 | 6.5 | 3.3 | 3.2 | 49.2308 | 73 | 33974.784 | 5715 |  | 14427.648
2017-01-18 |  | 24 | GDP cr unit 2 | 5.5 | 5.9 | 2.3 | 3.6 | 61.0169 | 73 | 38221.632 | 5715 | BOTH UNITS ON | 16231.104
2017-02-04 |  | 24 | FAP CR unit 1 | 5.5 | 4.2 | 2.41 | 1.79 | 42.619 | 56 | 14578.9056 | 5715 | BOTH UNITS ON | 8070.4656
2017-02-01 |  | 24 | Pestillator CR | 5.5 | 6.44 | 3.2 | 3.24 | 50.3106 | 59 | 27802.3104 | 5715 | BOTH UNITS ON | 14607.9936
2017-02-01 | 2017-02-01 | 24 | admin cold storage 1st flr unit-3 | 8.75 | 2.4 | 1.8 | 0.6 | 25 | 59 | 5148.576 | 5715 | all 3 are running | 2705.184
[9 empty] | Total | 432346.7246 | 74295 |  | 96151.2566
2017-01-10 |  | 12 | Near lift | 11 | 200 | 170 | 30 | 15 | 1 | 1800 | 5715 | comp-2 in line | 45813.6
2017-01-10 |  | 12 | pantry | 5.5 | [6 empty] | 5715 | in line
2017-01-10 |  | 12 | office-2 | 11 | [6 empty] | 5715 | comp-2 in line
2017-01-18 |  | 12 | kakade sir | 11 | [6 empty] | 5715 | comp-1 in line
2017-01-18 |  | 24 | server room | 1.5 | [6 empty] | not installed | not installed
2017-01-18 |  | 12 | Reception | 5.5 |  |  | 0 | #DIV/0! | 73 | 0 | 5715 | unit removed on 4 feb | 0
2017-01-18 |  | 24 | GLC lab | 5.5 | 6.5 | 3.3 | 3.2 | 49.2308 | 73 | 28032 | 5715 |  | 6050.304
2017-01-18 |  | 24 | GDP cr unit 2 | 5.5 | 5.9 | 2.3 | 3.6 | 61.0169 | 73 | 31536 | 5715 | BOTH UNITS ON | 6806.592
2017-02-01 |  | 24 | Pestillator CR | 5.5 | 6.44 | 3.2 | 3.24 | 50.3106 | 59 | 22939.2 | 5715 | BOTH UNITS ON | 12052.8
2017-02-04 |  | 24 | FAP CR unit 1 comp 2 | 5.5 | 4.2 | 2.41 | 1.79 | 42.619 | 56 | 12028.8 | 5715 | unit 1,2 both running | 6658.8
Note on G12: room set temp 24,saver is in bypass mode
Note on H12: room remote set temp 23 Saver Room temp 24 coil temp 12