## Sheet1
Instrument index for Catalyst High Pressure Dosing
Sr.No. | Tag | DCS Tag No | Type of Instruments | Description | I/O list | Line size | Remark
1 | XV Cat Mix | XV-307 | ON-OFF Valve | Catalyst Mixing | DO | 2" | Checked Found OK
2 | XV Vac | XV-302 | ON-OFF Valve | Vaccum | DO | 1" | Solenoid is Hand Operated with F/B on DCS-Checked OK
3 | XV Vent | XV-303 | ON-OFF Valve | Vent Line | DO | 1" | Solenoid is Hand Operated with F/B on DCS-Checked OK
4 | XV N2 | XV-301 | ON-OFF Valve | Nitrogen | DO | 1" | Solenoid is Hand Operated with F/B on DCS-Checked OK
5 | XV Pre Equa | XV-308 | ON-OFF Valve | Pressure Equalizer reactor V-701A | DO | 2" | Checked OK
6 | XV Pre Equa | XV-321 | ON-OFF Valve | Pressure Equalizer reactor V-701B | DO | 2" | Checked OK
7 | XV Dos Rea | XV-309 | ON-OFF Valve | Dossing vessal to reactor V-701A | DO | 2" | Checked OK-F/b is having some problem-correction is in progress
8 | XV Dos Rea | XV-323 | ON-OFF Valve | Dossing vessal to reactor V-701B | DO | 2" | Checked OK-F/b is having some problem-correction is in progress
Note: | All Dosing system valves having 300# flange rating
DCS configuration is already done on DCS
DCS graphics modification required.
Valves needs to check for leakage

## Valve Details
H2 LOOP REACTOR XV DETAILS
Sr.No. | Tag | DCS Tag No | Type of Instruments | Description | Valve Type | Act. Type | size | size | Rating | Body/yoke material | Trim Material | CV | Chara. | Leak Class | Spring Range | Failure Position | Packing | Sr.No. | Supply Press. | Limited Stroke | REMARK
1 | XV N2 | XV-301 | ON-OFF Valve | Nitrogen | 241-1 | 271 | 240CM2 | 1" | 300# | A351CF3M | SS316L | 12 | ON/OFF | VI | 0.9 - 3.3 Bar | Close | GRA | 890-26967 | 3.5 Bar | 15MM | 15MM
2 | XV Vac | XV-302 | ON-OFF Valve | Vaccum | 241-1 | 271 | 350CM2 | 2" | 300# | A351CF3M | SS316L | 47 | ON/OFF | VI | 2.1 - 3.3 Bar | Close | GRA | 890-26968 | 3.5 Bar | 15MM | 15MM
3 | XV Vent | XV-303 | ON-OFF Valve | Vent Line | 241-1 | 271 | 350CM2 | 2" | 300# | A351CF3M | SS316L | 47 | ON/OFF | VI | 2.1 - 3.3 Bar | Close | GRA | 890-26969 | 3.5 Bar | 15MM | 15MM
4 | XV Cat Mix | XV-307 | ON-OFF Valve | Catalyst Mixing | 241-1 | 271 | 240 CM2 | 1" | 300# | A351CF3M | SS316L | 12 | ON/OFF | VI | 0.9 - 3.3 Bar | Close | PTFE | 890-26957 | 3.5 Bar | 15MM | Valve passing checked @ 28 Bar(G) found okay & observed no any passing as on 22.08.2016
5 | XV Pre Equa | XV-308 | ON-OFF Valve | Pressure Equalizer reactor V-701A | 241-1 | 271 | 240 CM2 | 1" | 300# | A351CF3M | SS316L | 12 | ON/OFF | VI | 0.9 - 3.3 Bar | Close | PTFE | 890-26958 | 3.5 Bar | 15MM | Valve passing checked @ 28 Bar(G) found okay & observed no any passing as on 22.08.2016
6 | XV Dos Rea | XV-309 | ON-OFF Valve | Dossing vessal to reactor V-701A | 241-1 | 271 | 350 CM2 | 2" | 300# | A351CF3M | SS316L | 47 | ON/OFF | VI | 2.1 - 3.3 Bar | Close | PTFE | 890-26961 | 3.5 Bar | 15MM | 15MM
7 | XV Pre Equa | XV-321 | ON-OFF Valve | Pressure Equalizer reactor V-701B | 241-1 | 271 | 240 CM2 | 1" | 300# | A351CF3M | SS316L | 12 | ON/OFF | VI | 0.9 - 3.3 Bar | Close | PTFE | 890-26959 | 3.5 Bar | 15MM | 15MM
8 | XV Dos Rea | XV-323 | ON-OFF Valve | Dossing vessal to reactor V-701B | 241-1 | 271 | 350 CM2 | 2" | 300# | A351CF3M | SS316L | 47 | ON/OFF | VI | 2.1 - 3.3 Bar | Close | PTFE | 890-26964 | 3.5 Bar | 15MM | 15MM