## Data
|  | JST and C-303 CT | Fatty Acid CT | Postcon CT | GDP CT
Heat Load | TR | 926 | 1072 | 397 | 860
Circulation rate | m3/hr | 700 | 540 | 300 | 650
CT Delta T | °C | 4.0003 | 6.0032 | 4.0018 | 4.001
No. of Fans |  | 2 | 3 | 1 | 1
CT fan Tag No. |  | CT fan 1, 2 | CT fan | CT fan 3 | K3 CT fan
Fans KW |  | 11 | 15 | 18.5 | 30
No of Pumps (op+sb) |  | 2+2 | 3+1 | 1+1 | 2+2
Pumps Tag No. |  | P-362 A/B/C/D | P-903 A/B/C/D | P-364 A/B | P-9002 A/B, 20P03B
Rated Flow (One pump) | m3/hr | 450,450,200,? | 300 | 300 | 500500435
Rated head (One pump) | m | 50,50,50,? | 45 | 50 | 45,45,60
Motor power (One pump) | KW | 90,90,45,75 | 75 | 75 | 90,80,110
Cooling water user sections |  | JST | C-301 | Postcon | GDP
|  | C-303 | C-302 |  | Precon
|  | New SPD | Section 4 |  | Old SPD
|  |  | Section 5 |  | MCT Bleacher
|  |  | Loop reactor |  | GDU
|  |  | Lurgi |  | K4 vent condenser

## JST CT sketch
Cooling water side details of users
| CW flow rate | CW Tin | CW Tout | Heat Load | HTA
| Kg/hr | °C | °C | TR | m2
E-103 | 87680 | 32 | 40 | 231.9577 | 53.75
E-104 | 179000 | 32 | 40 | 473.545 | 10
E-105 | 193150 | 32 | 36 | 255.4894 | 68.5
JST + C-303
Cooling Tower
P-362 A
P-362 B
P-362 C
P-362 D
To C-303
Heat
Exchangers
E-103
E-105
E-104
JST CW supply line
JST CW return line
C-303 CW supply line

## C-303 CT sketch
P-362 A Current | 86 Amp
Full load current of motor |  | 150 Amp
JST + C-303
Cooling Tower
P-362 A
P-362 B
P-362 C
P-362 D
To JST
Heat exchangers
PHE
Threeway
CV

## Postcon CT sketch
Cooling water side details of users
| CW flow rate | CW Tin | CW Tout | Heat Load | HTA
| Kg/hr | °C | °C | TR | m2
PHE | 343800 | 33 | 40 | 795.8333 | 53.75
Cooling Tower
P-364 A
P-364 B
JST CW supply line
JST CW return line
C-303 CW supply line
PHE
Vapours from
Alfa laval calandriya 4
vapor saparator
To Vacuum
pump

## GDP CT sketch
GDU condenser
Postcon condenser
Cooling water side details of users
|  | CW flow rate | CW Tin | CW Tout | Heat Load | HTA | Inlet Line Size
|  | Kg/hr | °C | °C | TR | m2
Precon Surface condenser |  | 310434 | 32 | 37 | 513.2837
GDU condenser |  | Not in use + data not available
K4 vent condenser |  | 30000 | 32 | 37 | 49.6032
Old SPD PHE |  | 252448 | 32 | 37 | 417.4074
Bleacher condenser | [6 empty] | 2"
E-104 |  | 84100 | 36 | 39 | 83.4325 | 22.63
E-105 | [5 empty] | 67 | 3"
E-106 | [6 empty] | 2"
E-114 |  | 46000 | 36 | 39 | 45.6349 | 25.5
E-115 |  | 15300 | 36 | 39 | 15.1786 | 3.75
P-9002 B
Paharpur Cooling Tower
20P03 A
20P03 B
P-9002 A
To E-104
To E-105
To E-106
To E-114
To E-115
K4 vent
condenser
Old SPD PHE
Bleacher
condenser (E-763)

## GDP CT to SPD, MCT, PRECON prop
Proposal
Use of fatty acid cooling tower for Old SPD, MCT Bleacher and Precon inplace of GDP cooling when GDP is not running and load on fatty acid cooling tower is low
Benefit
GDP cooling tower will not be required to run when GDP is not running
Cooling tower fan power saving
Cooling tower pumps power saving
Savings
| No of days in year for saving | 80 | Days | (assumed)
| Cooling tower fan power saving | 11 | KW
| Pump power saving | 10 | KW | (assumed)
| Total yearly saving | 225388.8 | Rs/year
Data Analysis
Precon heat Load (When only Lurgi is running)
| Lurgi feed rate | MT/hr | 10
| Sweet water inlet to precon | MT/hr | 8.06
| Precon inlet concentration | % | 15
| Precon outlet concentration | % | 25
| Total water removed in precon | MT/hr | 3.224
| Water removed in last effect | MT/hr | 1.0747
| Heat load on last effect | Kcal/hr | 565274.6667
| Delta T in cooling tower | °C | 4
| Cooling water flow requirment | m3/hr | 141.3187
MCT Bleacher heat load
For E-763 (Vapour condenser)
| Cooling water inlet |  | 2 | inch
| Max flow rate of water through 2" line |  | 14 | m3/hr
Assuming 5°C DeltaT
| Heat load of E-763 |  | 70000 | Kcal/hr
Old SPD heat load
PHE detail:
| Make | Alfa Laval
| Type | M10 MFM
| Serial no. | 30112-95-896
| Year | 2009
| Inlet and outlet nozzle size | 4"
| Approx heat load | 600000 | Kcal
For All three
| Total Flow required | 280 | m3/hr
Costing
Mechanical material cost
|  | Unit | quantity | Unit price | Cost
| Pipe 10", CS, Sch 40 | m | 36 | 4000 | 144000
| Valve, Gate, 10", CS, 150#, FE | Nos | 2 | 50000 | 100000
| 10" Tee, CS, sch 40 | Nos | 2 | 3000 | 6000
| 10 X6" tee, CS, sch 40 | Nos | 2 | 2000 | 4000
| Elbow 10", CS, sch 40 | Nos | 8 | 4000 | 32000
| Pipe 6" CS, sch 40 | m | 30 | 2000 | 60000
| Elbow 6", CS, sch 40 | Nos | 5 | 1050 | 5250
| Tee 6 X6", CS, sch 40 | Nos | 1 | 1400 | 1400
| Valve Gate, 6", CS, 150#, FE | Nos | 2 | 19000 | 38000
|  | Total |  |  | 390650
|  | Tax | (@25%) |  | 97662.5
|  | Total cost including tax |  |  | 488312.5
Mechanical service cost
B. Mechanical Service Cost
| Description | Unit | QTY | Unit Rate | Total rate
| Pipe erection | INM | 540 | 48 | 25920
| SS Welding Joint | IND | 387.4 | 200 | 77480
| DP test | IND | 387.4 | 30 | 11622
| valve erection | IND | 16 | 184 | 2944
|  | Total material cost |  |  | 92046
|  | Tax | @25%) |  | 13806.9
|  | Total cost including tax |  |  | 105852.9
|  | Total Investment |  |  | 594165.4
|  | ROI | (In Months) |  | 31.6342