## MOC
Pump calculated power
Name of equipment | P20P03 | P9002A | P9002B | P 364 | Pharpur CT fan | Alpha Laval CT fan
calculated power | 135.8742 | 79.6717 | 80.2893 | 71.6428 | 28 | 18.5
127.2277
Month | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01
Power Cost Rs/KWH | 5.66 | 6.18 | 6.06 | 5.99 | 5.9
Date | Working Hrs |  |  | Plants Running |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  |  |  | GDP | Alfalaval
2016-11-22 | 8 |  |  | Stopped | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.019283
2016-11-23 | 24 |  |  | Stopped | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.05785
2016-11-24 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-25 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-26 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-27 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-28 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-29 | 24 |  |  | Stopped | on | P20P03 & P364 | Paharpur CT & Alfalaval | no saving | no saving | #VALUE!
2016-11-30 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.046104
0.73549
Date | Working Hrs |  |  | Plants Running |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  |  |  | GDP | Alfalaval
2016-12-01 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-02 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-03 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-04 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-05 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-06 | 24 |  |  | on | on | P20P03 & P9002A & B | Paharpur CT | 315.1886 | 334.3063 | 19.1176 | 0.028355
2016-12-07 | 24 |  |  | on | on | P20P03 & P9002A & B | Paharpur CT | 315.1886 | 334.3063 | 19.1176 | 0.028355
2016-12-08 | 24 |  |  | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014615
2016-12-09 | 24 |  |  | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014615
2016-12-10 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-11 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-12 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-13 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-14 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-15 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-16 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-17 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-18 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-19 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-20 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-21 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-22 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-23 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-24 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-25 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-26 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-27 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-28 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-29 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-30 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-31 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2.581
Date | Working Hrs | Plants Running |  |  |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  | JST | LST | GDP | Alfalaval
2017-01-01 | 24 | on | on | on | on | 20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.061938
2017-01-02 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-03 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-04 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-05 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-06 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-07 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-08 | 24 | Stopped | on | on | on | 20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.061938
2017-01-09 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-10 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-11 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-12 | 24 | on | on | on | on | P9002B & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-13 | 24 | on | on | on | on | P9002B & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-14 | 24 | on | on | on | on | P9002A & B &20P03 | Paharpur CT | 315.1886 | 334.3063 | 19.1176 | 0.027805
2017-01-15 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13021
2017-01-16 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-17 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-18 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-19 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-20 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-21 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-22 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-23 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-24 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-25 | 24 | Stopped | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-26 | 24 | Stopped | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-27 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-28 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
2017-01-29 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
2017-01-30 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
2017-01-31 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
1.5249
Date | Working Hrs | Plants Running |  |  |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  | JST | LST | GDP | Alfalaval
2017-02-01 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-02 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-03 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-04 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-05 | 24 | Stopped | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-06 | 24 | Stopped | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-07 | 24 | Stopped | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-08 | 24 | on | on | on | Stopped | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-09 | 24 | on | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-10 | 24 | on | on | on | on | P9002A& B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014165
2017-02-11 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-12 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-13 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-14 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-15 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-16 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-17 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-18 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-19 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-20 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-21 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-22 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-23 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-24 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-25 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-26 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-27 | 24 | Stopped | on | on | Stopped | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-28 | 24 | Stopped | on | on | Stopped | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2.4663
Date | Working Hrs | Plants Running |  |  |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  | JST | LST | GDP | Alfalaval
2017-03-01 | 24 | Stopped | on | on | Stopped | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-02 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-03 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-04 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-05 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-06 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-07 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-08 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-09 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-10 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-11 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-12 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-13 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-14 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-15 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-16 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-17 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-18 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-19 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-20 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-21 | 24 | Stopped | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-22 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-23 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-24 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-25 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-26 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-27 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-28 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-29 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-30 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-31 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2.1466
Note on C6: Amey Deshpande: If running with another pump
Note on C7: Amey Deshpande: If running single

## VAM
Sr. No. | SH1
Project: | VAM chilled water to GDP
Project Owner: | Shrish
Potential Saving in Rs Lac: | 23.6988 | Estimated Expense in Rs Lac: | 6 | Net Saving in FY16-17 in Rs Lac : | 13.2741
Base Data:
Power consumption before modification
Chiller A Power consumption |  |  | KW | 44 | Measured
Chiller B Power consumption |  |  | KW | 44 | Measured
Chiller Pump- P-7126A Power consumption |  |  | KW | 8 | Measured
Chiller Pump- P-7126B Power consumption |  |  | KW | 2 | Measured
Chiller Pump- P-7126D Power consumption |  |  | KW | 9 | Measured
Total present power consumption |  |  | KW | 107 | Calculated
Power consumption after modification
Power consumption by booster pump |  |  | KW | 20 | Estimated
Net Power saving |  |  | KW | 87 | Calculated
Power Cost |  |  | Rs/KW | 5
Total Running days per year |  |  | Days | 227 | Estimated
Net Saving |  |  | Rs/annum | 2369880 | Calculated
Total saving |  |  | Rs/annum | 23.6988 | Calculated
Run hr | [9 empty] | 76.55 | 432 | 93
Power cost | [9 empty] | 6.06 | 5.99 | 5.9
Saving per hr (base on actual KW data ) | [9 empty] | 76.66 | 76.66 | 76.66
| April | May | June | July | August | September | October | November | December | January | February | March
Saving achieved in Lac | 76.66 January: 0.35562; 76.66 February: 1.9837; 76.66 March: 0.42063
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das

## Paharpur CT Fan
BASE DATA
Initial power consumtion of paharpur CT fan | 30.8805 | KWH
Power consumtion of Paharpur CT fan after fan angles changed | 17.9107 | KWH
Power saving due to proposed modification | 12.9698 | KWH
Average power cost | 5.5 | Rs/KWH
Annual Savings | 5.6496 | Lacs
Power cost | [5 empty] | 5.2533 | 5.3357 | 5.9258 | 5.8751 | 6.0616 | 5.9833 | 5.8983
No of working days | 0 | 0 | 0 | 0 | 0 | 30 | 31 | 30 | 31 | 31 | 28 | 31
| April | May | June | July | August | September | October | November | December | January | February | March
Saving achieved in Lac | 0 | 0 | 0 | 0 | 0 | 0.49057 | 0.51487 | 0.55337 | 0.56692 | 0.58491 | 0.52149 | 0.56916

## HP steam saving
4078
SNOP plan Consumption | [11 empty] | 0.40043
FEED Oil For LST | April | May | June | July | Aug | Sep | Oct | Nov | December | January | Feb | maR | Total | Specific | apr | may | june | july | Aug | Sept | Oct | Nov | dec | Jan | feb | March.17 | Total | Specific | Average | Specific
PFAD |  | 299.15 |  | 917.547 | 954.116 |  |  | 1276.046 | 2901.772 | 1398.575 | 430.11 | 2007.63 | 10184.946 |  | 1021.891 | 2143.418 | 429.511 |  | 922.854 |  | 1049.095 | 678.89 | 357.43 | 353.402 | 1199.548 |  | 8156.039 |  | 1685.8113
HP Steam (MT) ( FIQ 26 ) |  | 30.821 |  | 115.464 | 159.798 |  |  | 199.665 | 250.221 | 450 | 80.8 | 263.8 | 1550.569 | 152.2413 | 187 | 350.792 | 44.8 |  | 119.604 |  | 105.749 | 82.042 | 47.53 | 42.74 | 148.41 |  | 1128.667 | 138.3842 | 246.5233 | 0.14623 | 233948.5937
| May: 0.10303 | [15 empty] | 90.898
MP Steam |  | 29.3878 |  | 42.8855 | 93.6615 |  |  | 283.305 | 451.148 | 465 | 186 | 546.78 | 2098.1678 |  | 297.3 | 448.3 | 100.327 |  | 146.49 |  | 214.192 | 98.647 | 77.307 | 29972.5 | 210058.7343 |  | 241413.7973 | % | 348.6812 | 0.20683
NG for steam (SCM) | May: 7196.3335; July: 14207.1171; Aug: 22740.3863; Nov: 45065.3511; December: 20523177.2512 | 20612386.4394 |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 72737 | 358469.7997 |  | 431206.7997 |  | 3171136.3753 | 1881.0743
Water (MT) ( FIQ 06 ) |  | 200.342 |  | 561.017 | 625.707 |  |  | 846.294 | 1823.069 | 992.967 | 298.553 | 1397.34 | 6745.289 |  | 804.812 | 1344.069 | 335.094 |  | 598.265 |  | 17760.013 | 432.788 | 218.361 | 196.6503 | 786.271 |  | 22476.3233 |  | 2186.4987 | 1.297
Power (kWh) |  | 16160.4033 |  | 25976.225 | 38261.2064 |  |  | 129776.5477 | 241836.1965 | 145567.1045 | 43638.1528 | 123336 | 764551.8362 |  | 56952.4902 | 103922.0549 | 37800.0548 |  | 84422.2291 |  | 63765.0802 | 41264.4587 | 21980.0872 | 14239.8089 | 85169.0894 |  | 509515.3533 |  | 121200.633 | 71.8945
MCT | July: 448.623; Aug: 329.188; Oct: 92.92; Nov: 347.131; December: 278.827; 0.40043 maR: 372.48 | [8 empty] | 295.739 |  | 401.6 | [5 empty] | 320.8135
HP Steam (MT) ( FIQ 26 ) | July: 102.407; Aug: 70.001; Oct: 37.653; Nov: 64.048; December: 64.632; 0.40043 maR: 93.587 | [8 empty] | 58.14 |  | 74.454 | [5 empty] | 70.6153 | 0.22011
MP Steam | July: 47.9828; Aug: 29.808; Oct: 9.58; Nov: 109.661; December: 118.87; 0.40043 maR: 165.11 | [8 empty] | 44.057 |  | 65.072 | [5 empty] | 73.7676 | 0.22994
NG for steam (SCM) | July: 13492.9714; Aug: 8954.8635; Oct: 4407.2546; Nov: 16208.5783 | [8 empty] | 0 |  | 41563 | [5 empty] | 14104.4446 | 43.9646
Water (MT) ( FIQ 06 ) | July: 335.835; Aug: 217.605; Oct: 70.087; Nov: 244.095; December: 223.15; 0.40043 maR: 433.67 | [8 empty] | 220.443 |  | 310.617 | [5 empty] | 256.9377 | 0.80089
Power (kWh) | July: 22543.8367; Aug: 17247.551; Oct: 15554.4032; Nov: 52512.196; December: 47580.3061; 0.40043 maR: 39367.1 | [8 empty] | 33752.1062 |  | 24937.1772 | [5 empty] | 31686.8346 | 98.7703
Mustard Residue | July: 562.44; Aug: 127.74; Sep: 913.08; Nov: 747.23 |  |  |  | 1216.344 |  |  | 587.998 |  |  |  | 495.139 | [5 empty] | 664.2816
HP Steam (MT) ( FIQ 26 ) | July: 77.348; Aug: 24.139; Sep: 245.4; Nov: 103.867 |  |  |  | 134423 |  |  | 71625 |  |  |  | 55699 | [5 empty] | 37456.822 | 56.387
MP Steam | July: 60.7675; Aug: 26.9382; Sep: 246.75; Nov: 141.1915 |  |  |  | 275520.7586 |  |  | 100365 |  |  |  | 71480.48 | [5 empty] | 63977.4123 | 96.3107
NG for steam (SCM) | July: 12391.7227; Aug: 4582.6464; Sep: 46418.2822; Nov: 22866.1146 |  |  |  | 0 |  |  | 0 |  |  |  | 0 | [5 empty] | 12322.6808 | 18.5504
Water (MT) ( FIQ 06 ) | July: 353.124; Aug: 116.644; Sep: 617.182; Nov: 474.704 |  |  |  | 797.673 |  |  | 414.44 |  |  |  | 347.206 | [5 empty] | 445.8533 | 0.67118
Power (kWh) | July: 22766.866; Aug: 8445.058; Sep: 118234.71; Nov: 80966.0683 |  |  |  | 76306.9245 |  |  | 49679.1718 |  |  |  | 25933.8006 | [5 empty] | 54618.9427 | 82.2226
RMO | 1484.263 | 2713.517 | 1724.149 |  |  | 928.079 | 1315.4 |  |  | 1002.646 | 866.545 | 2950 | 12984.599 |  | 3337.898 | 1304.946 | 1111.523 |  | 1088.231 | 565.7243 | 146.319 |  | 1402.554 | 942.025 | 1085.617 | 1262.511 | 12247.3483 |  | 2182.8996
HP Steam (MT) ( FIQ 26 ) | 234.552 | 403.3 | 307.34 |  |  | 198.606 | 328.955 |  |  | 202.257 | 160.8 | 395.15 | 2230.96 | 171.8159 | 447 | 195.5 | 149 |  | 136.649 | 89.185 | 36.378 |  | 182.016 | 129.648 | 176.7 | 166.985 | 1709.061 | 139.5454 | 345.2626 | 0.15817 | 818121.2136
MP Steam | 102.403 | 190.4258 | 200.3136 | 6.8647 |  | 309.5 | 320.129 |  |  | 421.623 | 161.4 | 500.542 | 2213.2011 |  | 785 | 460.7 | 139.7 |  | 100.527 | 103.087 | 31.617 |  | 154.433.1 | 111356.25 | 255864.16 | 231689.41 | 600530.451 | 81.218 | 377.9396 | 0.17314
NG for steam (SCM) | April: 30231.6041; May: 56906.1481; June: 47385.941; July: 1632.1548; Sep: 48181.2451; Oct: 58866.6191 | 243203.7123 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 241004.25 | 432575.16 | 398674.41 | 1072253.82 | % | 37415.9557 | 17.1405
Water (MT) ( FIQ 06 ) | 950.409 | 1741.051 | 1208.696 | 47.595 |  | 636.856 | 862.692 |  |  | 698.715 | 607.514 | 1935.5 | 8689.028 |  | 2258.024 | 817.338 | 774.97 |  | 977.849 | 410 | 133.2871 |  | 869.329 | 646.2816 | 845.55 | 830.1152 | 8562.7439 |  | 1389.3443 | 0.63647
Power (kWh) | 46943.45 | 90947.8504 | 71479.2525 | 2104.37 |  | 80500.5873 | 148415.22 |  |  | 103092.4912 | 45307.0327 | 16108 | 604898.2541 |  | 200049.7932 | 136508.9922 | 64556.507 |  | 44560.0486 | 46628.695 | 7264.2021 |  | 60047.2873 | 54305.2827 | 106466.9248 | 64354.0486 | 784741.7815 |  | 104083.0608 | 47.6811
RBDPS | July: 1464.304; Aug: 594.39; Sep: 1219.899; Oct: 1230.6; Nov: 1079.072; January: 469.442; Feb: 501.434 | 6559.141 |  |  |  |  | 655.416 |  |  |  |  | 994.9379 |  |  | 488.698 | 2139.0519 |  | 1476.8636
HP Steam (MT) ( FIQ 26 ) | July: 224.779; Aug: 118.977; Sep: 253.947; Oct: 247.504; Nov: 161.125; January: 93.159; Feb: 90 | 1189.491 | 181.3486 |  |  |  | 122.606 |  |  |  |  | 166.87 |  |  | 72.733 | 362.209 | 169.3316 | 259.0733 | 0.17542 | 53209.4642
MP Steam | July: 70.7131; Aug: 109.9507; Sep: 150.7816; Oct: 240.0845; Nov: 244.704; January: 137.634; Feb: 164.7 | 1118.5679 |  |  |  |  | 71488.8 |  |  |  |  | 123933.338 |  |  | 132617.63 | 328039.768 | 93.3735 | 19765.9274 | 13.3837
NG for steam (SCM) | July: 26511.5482; Aug: 47076.8632; Sep: 28973.5621; Oct: 54111.9778; Nov: 37867.417 | 194541.3684 |  |  |  |  | 0 |  |  |  |  | 0 |  |  | 205350.63 | 205350.63 | % | 48635.3421 | 32.9315
Water (MT) ( FIQ 06 ) | July: 1026.414; Aug: 441.229; Sep: 750.513; Oct: 818.435; Nov: 744.854; January: 325.331; Feb: 287.42 | 4394.196 |  |  |  |  | 489.496 |  |  |  |  | 719.21 |  |  | 341.839 | 1550.545 |  | 999.7098 | 0.67691
Power (kWh) | July: 37787.1483; Aug: 60943.058; Sep: 42176.4848; Oct: 124745.3; Nov: 101233.1194; January: 45887.3098; Feb: 45334.4981 | 458106.9184 |  |  |  |  | 30802.5564 |  |  |  |  | 49121.109 |  |  | 37605.5173 | 117529.1827 |  | 99613.7502 | 67.4495
[30 empty] | Total savings in RS | 1105279.2715
Steam ocost Rs.2.07 per MT