## Project 1
Project: | Utilities Leakages identification & prevention
Project Owner: | Prabhat Das
Potential Saving in Rs Lac: | 49.56 | Estimated Expense in Rs Lac: | 0 | Net Saving in FY16-17 in Rs Lac : | 30
Base Data:
HP steam loss@60 bar(G),1.5 mm bore dia | [5 empty] | 55.97 | kg/hr
no.of leakages in HP line | [5 empty] | 3
MP steam loss@12 bar(G),1 mm bore dia | [5 empty] | 24.87 | kg/hr
no.of leakages in HP line | [5 empty] | 4
MP steam loss@12 bar(G),3 mm bore dia | [5 empty] | 42.13 | kg/hr
no.of leakages in HP line | [5 empty] | 1
Total steam loss | [5 empty] | 309.52 | Kg/hr
Steam cost cost |  |  |  | 1.67 | 1.71 | 1.709 | 1.688 | 1.9 | 1.9 | 1.99 | 1.9767 | 2
No of working days |  |  |  | 10 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31
| April | May | June | July | August | September | October | November | December | January | February | March
Saving achieved in Lac | 0 | 0 | 0 | 0.77 | 3.9378 | 3.8086 | 3.8872 | 4.2342 | 4.3754 | 4.5826 | 4.1115 | 4.6057
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das

## Project 2
Project: | Thermic fluid header insulation
Project Owner: | Prabhat Das
Potential Saving in Rs Lac: | 22.6383 | Estimated Expense in Rs Lac: | 0.36 | Net Saving in FY16-17 in Rs Lac : | 15.09
Base Data:
Total uninsulated area (Excluding Flanges) | [5 empty] | 27.95 | m2
Total heat loss | [5 empty] | 192643.21 | kcal/hr
Coal consumption | [5 empty] | 57.3343 | kg/hr
Saving potential | [5 empty] | 0.062884 | Lacs/day
[6 empty] | 1.8865 | Lacs/month
[6 empty] | 22.6383 | Lacs/annum
Coal cost |  |  |  | 5.06 | 5.28 | 5.32 | 5.19 | 5.12 | 6.16 | 6.14 | 6.6 | 6.87
No of working days |  |  |  | 6 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31
| April | May | June | July | August | September | October | November | December | January | February | March
Saving achieved in Lac | 0 | 0 | 0 | 0.25066 | 2.2523 | 2.1961 | 2.2139 | 2.1136 | 2.6277 | 2.6191 | 2.5429 | 2.9305
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das

## Project 3
Project: | Cooling tower interconnection
Project Owner: | Prabhat Das
Potential Saving in Rs Lac: | 26.28 | Estimated Expense in Rs Lac: | 0.6 | Net Saving in FY16-17 in Rs Lac :
Base Data:
total energy consumed in cooling tower before interconnection | [5 empty] | 243.5 | kwh
total energy consumed in cooling tower after interconnection | [5 empty] | 153 | kwh
Energy saving | [5 empty] | 90.5 | kwh
No of working days assumed in a month | [5 empty] | 15 | days/month
Saving potential | [5 empty] | 1.7919 | Lacs/month
| April | May | June | July | August | September | October | November | December | January | February | March
Saving achieved in Lac | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26 | 2.58 | 1.52 | 2.47 | 2.15
Certified by process owner
Verified by Anirudh Bansod
Verified by Dinesh Danav
Verified by Prabhat Das