## Slide 1: Section 3 heat exchangers analysis

## Slide 2: Outline
Process flow diagram
Analysis
Expected results

## Slide 3: Process flow diagram

## Slide 4: PFD explanation
Based on above PFD
  Deterioration in performance of E-357 and E-358 directly increases load of E-359 (thermic fluid preheater)
  Similarly deterioration in performance of E-351, E-352 & E-353 directly increase load of E-354 (LP steam heater), however in case even after 100% opening of steam supply valve, enough temperature not achieve then this load also transfers to thermic fluid preheater

## Slide 5: E-357 Analysis
 |  | Design data |  |  | 8-Jun-16 |  |  | 10-Jun-16 | 
E-357 | Spiral | Cold Side | Hot Side |  | Cold Side | Hot Side |  | Cold Side | Hot Side
Fluid |  | FA | FA |  | FA | FA |  | FA | FA
Flow | Kg/hr | 30000 | 18200 |  | 22000 | 13650 |  | 21700 | 13086
Temp (in) | °C | 123.3 | 176 |  | 97.4 | 164.5 |  | 102.5 | 168.4
Temp (out) | °C | 153.4 | 128.6 |  | 125.1 | 114.8 |  | 130.9 | 116
Cp | Kcal/Kg°C | 0.6 | 0.6 |  | 0.6 | 0.6 |  | 0.6 | 0.6
Heat Load | Kcal/hr | 491728 | 517608 |  | 366339 | 407043 |  | 370281 | 411424
LMTD | °C | 12 |  |  | 27 |  |  | 24 | 
Area | m2 | 174.00 |  |  | 174.00 |  |  | 174.00 | 
HTC | Kcal/hrm2°C | 237 |  |  | 78 |  |  | 90 | 
 | W/m2K | 275 |  |  | 91 |  |  | 105 | 

## Slide 6: E-357 Analysis contd.
 |  | After cleaning | 
E-357 | Spiral | Cold Side | Hot Side
Fluid |  | FA | FA
Flow | Kg/hr | 22000 | 13650
Temp (in) | °C | 97.4 | 164.5
Temp (out) | °C | 132.7 | 104.5
Cp | Kcal/Kg°C | 0.6 | 0.6
Heat Load | Kcal/hr | 466830 | 491400
LMTD | °C | 16 | 
Area | m2 | 174.00 | 
HTC | Kcal/hrm2°C | 163 | 
 | W/m2K | 189 | 
Rise in feed temperature = 7.6 °C
Extra heat recovered = 0.12 Mkcal/hr
Cost saving = 12.1 Lacs Rs/year

## Slide 7: E-358 Analysis
 |  | Design data |  |  | 8-Jun-16 |  |  | 10-Jun-16 | 
E-358 | Spiral | Cold Side | Hot Side |  | Cold Side | Hot Side |  | Cold Side | Hot Side
Fluid |  | FA | FA |  | FA | FA |  | FA | FA
Flow | Kg/hr | 30000 | 9800 |  | 22000 | 6200 |  | 21700 | 4865
Temp (in) | °C | 149.2 | 257 |  | 125.1 | 225.1 |  | 130.9 | 220.6
Temp (out) | °C | 179.9 | 165 |  | 139.4 | 168.7 |  | 142.1 | 165.1
Cp | Kcal/Kg°C | 0.6 | 0.6 |  | 0.6 | 0.6 |  | 0.6 | 0.6
Heat Load | Kcal/hr | 513912 | 540960 |  | 188827 | 209808 |  | 145804 | 162005
LMTD | °C | 39 |  |  | 62 |  |  | 53 | 
Area | m2 | 45.30 |  |  | 45.30 |  |  | 45.30 | 
HTC | Kcal/hrm2°C | 293 |  |  | 67 |  |  | 60 | 
 | W/m2K | 341 |  |  | 78 |  |  | 70 | 

## Slide 8: E-358 analysis contd.
Rise in feed temperature = 7.4 °C
Extra heat recovered = 0.11 Mkcal/hr
Cost saving = 11.8 Lacs Rs/year
 |  | After cleaning | 
E-358 | Spiral | Cold Side | Hot Side
Fluid |  | FA | FA
Flow | Kg/hr | 22000 | 6200
Temp (in) | °C | 132.7 | 225.1
Temp (out) | °C | 154.7 | 143
Cp | Kcal/Kg°C | 0.6 | 0.6
Heat Load | Kcal/hr | 290141 | 305412
LMTD | °C | 31 | 
Area | m2 | 45.30 | 
HTC | Kcal/hrm2°C | 205 | 
 | W/m2K | 238 | 

## Slide 9: Expected results from cleaning
E-358 outlet temperature before cleaning = 139.4°C
E-358 outlet temperature after cleaning = 154.7 °C (Calculated)
Rise in feed temperature = 15.3 °C
Energy saving = 0.24 Mkcal/hr
Cost saving = 24.4 Lacs Rs/year
  (@5 Rs coal cost and 300 days running)

## Slide 10: Other benefits
Improvement in heat recovery will also reduce heat load of cooling towers
Similar results are expected from section 4 & 5 heat exchanger network (Data to be collected)
Way forward

## Slide 11: Section 4 heat exchangers analysis

## Slide 12: Taken for Study
E – 426 – Not in operation
E – 427 – analysis done
E – 406 – Data inconsistent. TT to be checked
E – 429 – Not in operation
E – 435 – analysis done

## Slide 13: E - 427 data & analysis
Analysis: Design HTC = 244 Kcal/hrm2°C
Actual HTC = 56 – 71 Kcal/hrm2°C
Supposed HTC for above feed rate = 121 – 136 Kcal/hrm2°C

## Slide 14: E - 406 data & analysis
Analysis: Hot side outlet temperature is below cold side inlet temperature,
Which indicate any one of these TT is malfunctioning

## Slide 15: E - 435 data & analysis
Analysis: Design HTC = 324 Kcal/hrm2°C
Actual HTC = 15 - 69 Kcal/hrm2°C
Supposed HTC for above feed rate = 160 - 181 Kcal/hrm2°C

## Slide 16: Section 5 heat exchangers analysis

## Slide 17: Taken for study
E – 102 – Insufficient data. TT not available
E – 105 – Insufficient data. TT not available
E – 402 – analysis based on approach temp
E – 104 – Data inconsistent. TT to be checked
E – 101 – analysis based on approach temp

## Slide 18: E - 102 data & analysis
Analysis: Data insufficient

## Slide 19: E - 105 data & analysis
Analysis: Data insufficient

## Slide 20: E - 402 data & analysis
Analysis: Design data not available.
Approach temperature value for above data are 29, 44, 56, 53
Approach temperature value is on higher side, for a properly design spiral
heat exchanger, this value usually lies in range of 5 to 15 °C

## Slide 21: E - 104 data & analysis
Analysis: Hot side outlet temperature is below cold side inlet temperature in one case
and very less difference in other cases. This indicate any one of these TT is malfunctioning

## Slide 22: E - 101 data & analysis
Analysis: Design data not available.
Approach temperature value for above data are 48, 37, 62, 16
Approach temperature value is on higher side, for a properly design spiral
heat exchanger, this value usually lies in range of 5 to 15 °C

## Slide 23: Thank You !!!