## Slide 1: Pump Efficiency Analysis
Data based on 17th & 18th Jun 2016

## Slide 2: P-01G14A (Tempered water pump-III)
Comparison between design and actual working parameters
Parameter | Unit | Design | Actual
Flow | M3/hr | 365.79 | 390
Differential head | M | 35 | 18.4 (Design Suction head is considered)
Power | KWH | 46.19 | 31
Efficiency | % | 83.9 | 70.08

## Slide 3
If pump will run at design efficiency then power consumption reduced to 25.89 KWH
Actual power consumption:31KWH
Saving potential: 31 - 25.89 =5.11KWH
Saving per annum: 5.11*24*330*4.67 = 1.88 lacs

## Slide 4: P-01G16A (Tempered water pump-II)
Comparison between design and actual working parameters
Parameter | Unit | Design | Actual
Flow | M3/hr | 225 | 225
Differential head | M | 42 | 42 (Design Diff head is considered)
Power | KWH | 36.67 | 46
Efficiency | % | 78 | 62.20
Note: Measured Discharge head is 45MWC

## Slide 5
If pump will run at design efficiency then power consumption reduced to 39.30 KWH
Actual power consumption:46KWH
Saving potential: 46 – 39.30 = 6.70KWH
Saving per annum: 6.70*24*330*4.67 = 2.47lacs

## Slide 6: P-05G10A (Tempered water pump-I)
Comparison between design and actual working parameters
Parameter | Unit | Design | Actual
Flow | M3/hr | 350 | 370
Differential head | M | 51 | 40.4
Power | KWH | 71.57 | 89
Efficiency | % | 75.5 | 50.85

## Slide 7
If pump will run at design efficiency then power consumption reduced to 59.94 KWH
Actual power consumption:89KWH
Saving potential: 89 – 59.94 = 29.06KWH
Saving per annum: 29.06*24*330*4.67 = 10.74 lacs

## Slide 8: P-05G9A (FAP Cooling tower)
Comparison between design and actual working parameters
Parameter | Unit | Design | Actual
Flow | M3/hr | 725 | 574
Differential head | M | 50 | 49
Power | KWH | 137.18 | 135
Efficiency | % | 80 | 63.08

## Slide 9
If pump will run at design efficiency then power consumption reduced to 106.44 KWH
Actual power consumption:135KWH
Saving potential: 135 – 106.44 = 28.56KWH
Saving per annum: 28.56*24*330*4.67 = 10.56 lacs

## Slide 10: P-362C (splitting + C-303 indirect CT)
Comparison between design and actual working parameters
Parameter | Unit | Design | Actual
Flow | M3/hr | 200 | 380
Differential head | M | 50 | 44
Power | KWH | 38.81 | 45.84
Efficiency | % | 78 (Assumed) | 110.43

## Slide 11
THANK YOU…..