## till Mar-2015 (hidden)
Month | Equipment | Planned | Completed | Slippage |  | Condition Monitoring of Bearing |  | Month | Equipment | Equipment Covered
2014-04-14 | Motor | 114 | 114 | 0 | 2015-09-14 | Bearing Replacement | 12
| Panel | 25 | 25 | 0 | 2015-04-14 | Bearing Replacement | 17
2014-05-14 | Motor | 118 | 118 | 0 | 2014-05-14 | Bearing Cm | 30 | 2014-05-14 | Thermography | 91
| Panel | 36 | 36 | 0 |  | Bearing Replacement | 5 |  | Greasing | 43
2014-06-14 | Motor | 119 | 119 | 0 |  | Planned for bearing replacement | 3 | 2014-06-14 | Thermography | NA
| Panel | 40 | 40 | 0 |  | Motor burnt | 2 |  | Greasing | 7
2014-07-14 | Motor | 118 | 112 | 6 | 2014-06-14 | Bearing Cm | 102 | 2014-07-14 | Thermography | NA
| Panel | 40 | 40 | 0 |  | Bearing Replacement | 9 |  | Greasing | 36
2014-08-14 | Motor | 117 | 115 | 2 |  | Planned for bearing replacement | 4 | 2014-07-14 | Thermography | NA
| Panel | 40 | 40 | 0 |  | Motor burnt | 1 |  | Greasing | 21
2014-09-14 | Motor | 120 | 120 | 0
| Panel | 38 | 38 | 0
2014-10-14 | Motor | 114 | 112 | 2 | 2014-07-14 | Bearing Cm | 0 | 2014-10-14 | Thermography | NA
| Panel | 25 | 25 | 0 |  | Bearing Replacement | 11 |  | Greasing | 56
2014-11-14 | Motor | 118 | 116 | 2 |  | Planned for bearing replacement | 0 | 2014-11-14 | Thermography | NA
| Panel | 37 | 37 | 0 |  | Motor burnt | 2 |  | Greasing | 13
2014-12-14 | Motor | 121 | 111 | 10 | 2014-08-01 | Bearing Cm | 27 | 2014-12-14 | Thermography | 91
| Panel | 39 | 39 | 0 |  | Bearing Replacement | 3 |  | Greasing | 69
2015-01-14 | Motor | 128 | 128 | 0 |  | Planned for bearing replacement | 0 | 2015-01-14 | Thermography | 0
| Panel | 40 | 40 | 0 |  | Motor burnt | 1 |  | Greasing | 30
2015-02-14 | Motor | 119 | 119 | 0 | 2014-10-14 | Bearing Cm | 30 | 2015-02-14 | Thermography | 0
| Panel | 40 | 40 | 0 |  | Bearing Replacement | 9 |  | Greasing | 0
2015-03-14 | Motor | 122 | 115 | 7 |  | Planned for bearing replacement | 0 | 2015-03-14 | Thermography | 92
| Panel | 38 | 38 | 0 |  | Motor burnt | 1 |  | Greasing | 40
[5 empty] | 2014-11-01 | Bearing Cm | 2
[6 empty] | Bearing Replacement | 7
[6 empty] | Planned for bearing replacement | 0
[6 empty] | Motor burnt | 3
[5 empty] | 2014-12-01 | Bearing Cm | 76
[6 empty] | Bearing Replacement | 6
[6 empty] | Planned for bearing replacement | 2
[6 empty] | Motor burnt | 3
[5 empty] | 2015-01-01 | Bearing Cm | 248
[6 empty] | Bearing Replacement | 11
[6 empty] | Planned for bearing replacement | 0
[6 empty] | Motor burnt | 0
[5 empty] | 2015-02-01 | Bearing Cm | 206
[6 empty] | Bearing Replacement | 16
[6 empty] | Planned for bearing replacement | 2
[6 empty] | Motor burnt | 0
[5 empty] | 2015-03-01 | Bearing Cm | 19
[6 empty] | Bearing Replacement | 4
[6 empty] | Planned for bearing replacement | 1
[6 empty] | Motor burnt | 2
Note on M7: electrical.taloja: Schedule is of 3months next is in Sep-14
Note on M8: electrical.taloja: Grease Gun is having problem
Note on M9: electrical.taloja: Schedule is of 3months next is in Sep-14
Note on M11: electrical.taloja: Schedule is of 3months next is in Sep-14
Note on M15: electrical.taloja: Schedule is of 3months next is in Jan-15
Note on M17: electrical.taloja: Schedule is of 3months next is in Jan-15
Note on M21: admin: Schedule is quarterly next is March-2015
Note on M23: admin: Next schedule is MAR-2015

## till apr-2015 (hidden)
Month | Equipment | Planned | Completed | Slippage | Condition Monitoring of Bearing |  |  | Month | Equipment | Equipment Covered | Month | Equipment | Nos/status
2015-04-14 | Motor | 120 | 111 | 9 | 2015-04-14 | Bearing Cm | 85 | 2015-04-14 | Thermography | 0 | 2015-04-14 | Maintenance free battery | 16
| Panel | 25` | 25 | 0 |  | Bearing Replacement | 4 |  | Greasing | 14 |  | Distilled water battery | 9*2times
2015-05-14 | Motor | 125 | 123 | 2 |  | Planned for bearing replacement | 0 | 2015-05-14 | Thermography | 92(internal) & 62(External) |  | Emergency Light trial | Ok
| Panel | 33 | 33 | 0 |  | Motor burnt | 1 |  | Greasing | 25 | 2015-05-14 | Maintenance free battery | NA
2015-06-14 | Motor | 122 | 119 | 3 | 2015-05-14 | Bearing Cm | 124 | 2015-06-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 37 | 0 | 0 |  | Bearing Replacement | 10 |  | Greasing | 45 |  | Emergency Light trial | Ok
2015-07-14 | Motor | 121 | 121 | 0 |  | Planned for bearing replacement | 0 | 2015-07-14 | Thermography | 0 |  | Transformer PM | 6
| Panel | 40 | 40 | 0 |  | Motor burnt | 1 |  | Greasing | 26 | 2015-06-14 | Maintenance free battery | NA
2015-08-14 | Motor | 119 | 119 | 0 | 2015-06-14 | Bearing Cm | 110 | 2015-08-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 38 | 38 | 0 |  | Bearing Replacement | 7 |  | Greasing | 25 |  | Emergency Light trial | Ok
2015-09-14 | Motor | 121 | 121 | 0 |  | Planned for bearing replacement | 0 | 2015-09-14 | Thermography | 98 | 2015-07-14 | Maintenance free battery | 15
| Panel | 34 | 34 | 0 |  | Motor burnt | 2 |  | Greasing | 43 |  | Distilled water battery | 9*2times
2015-10-14 | Motor | 113 | 112 | 1 | 2015-07-14 | Bearing Cm | 54 | 2015-10-14 | Thermography | 0 |  | Emergency Light trial | Ok
| Panel | 25 | 34 | 0 |  | Bearing Replacement | 11 |  | Greasing | 13 | 2015-08-14 | Maintenance free battery | NA
2015-11-14 | Motor | 120 | 115 | 4 |  | Planned for bearing replacement | 0 | 2015-11-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 34 | 34 | 0 |  | Motor burnt | 1 |  | Greasing | 44 |  | Emergency Light trial | Loop reactor fitting problem rest ok
2015-12-14 | Motor | 127 | 127 | 0 | 2015-08-14 | Bearing Cm | 115 | 2015-12-14 | Thermography | 1 |  | Transformer PM | 7
| Panel | 27 | 27 | 0 |  | Bearing Replacement | 5 |  | Greasing | 59 | 2015-09-14 | Maintenance free battery | NA
2016-01-01 | Motor | 118 | 118 | 0 |  | Planned for bearing replacement | 5 | 2016-01-01 | Thermography | 87 |  | Distilled water battery | 9*2times
| Panel | 31 | 31 | 0 |  | Motor burnt | 0 |  | Greasing | 10 |  | Emergency Light trial | CPP PMCC, Jutasama 3rd floor,Syndet 1st floor problem rest ok
2016-02-02 | Motor | 123 | 122 | 1 | 2015-09-14 | Bearing Cm | 0 | 2016-02-01 | Thermography | 96 |  | Transformer PM | NA
| Panel | 38 | 38 | 0 |  | Bearing Replacement | 5 |  | Greasing | 67 |  | Earthing Pit PM | OK
2016-03-02 | Motor | 123 | 123 | 0 |  | Planned for bearing replacement | 2 |  |  |  | 2015-10-14 | Maintenance free battery | 16
| Panel | 34 | 34 | 0 |  | Motor burnt | 2 |  |  |  |  | Distilled water battery | 9*2times
[5 empty] | 2015-10-14 | Bearing Cm | 123 |  |  |  |  | Emergency Light trial | FAP 2nd floor CFL Fitting N/W rest ok
[6 empty] | Bearing Replacement | 8 |  |  |  |  | Transformer PM | NA
[6 empty] | Planned for bearing replacement | 0 |  |  |  |  | Earthing Pit PM | NA
[6 empty] | Motor burnt | 1 |  |  |  | 2015-11-14 | Maintenance free battery | NA
[5 empty] | 2015-11-14 | Bearing Cm | 0 |  |  |  |  | Distilled water battery | 10*2times
[6 empty] | Bearing Replacement | 8 |  |  |  |  | Emergency Light trial | Ok 24.11.15
[6 empty] | Planned for bearing replacement | 2 |  |  |  |  | Transformer PM | 8
[6 empty] | Motor burnt | 0 |  |  |  |  | Earthing Pit PM | NA
[5 empty] | 2015-12-14 | Bearing Cm | 72 |  |  |  | 2015-12-14 | Maintenance free battery | NA
[6 empty] | Bearing Replacement | 8 |  |  |  |  | Distilled water battery | 9*2times
[6 empty] | Planned for bearing replacement | 0 |  |  |  |  | Emergency Light trial | Ok 27.12.15
[6 empty] | Motor burnt | 0 |  |  |  |  | Transformer PM | NA
[5 empty] | 2015-01-01 | Bearing Cm | 101 |  |  |  |  | Earthing Pit PM | NA
[6 empty] | Bearing Replacement | 6 |  |  |  |  | Fire Alarm | OK
[6 empty] | Planned for bearing replacement | 0 |  |  |  | 2016-01-01 | Maintenance free battery | 15
[6 empty] | Motor burnt | 0 |  |  |  |  | Distilled water battery | 10*2times
[5 empty] | 2015-02-01 | Bearing Cm | 15 |  |  |  |  | Emergency Light trial | Ok 20.1.16
[6 empty] | Bearing Replacement | 14 |  |  |  |  | Transformer PM | NA
[6 empty] | Planned for bearing replacement | 0 |  |  |  |  | Earthing Pit PM | NA
[6 empty] | Motor burnt | 0 |  |  |  | 2016-02-01 | Maintenance free battery | 0
[5 empty] | 2015-03-01 | Bearing Cm | 227 |  |  |  |  | Distilled water battery | 10*2times
[6 empty] | Bearing Replacement | 13 |  |  |  |  | Emergency Light trial | Ok 24.2.16
[6 empty] | Planned for bearing replacement | 2 |  |  |  |  | Transformer PM | Ok 10.2.16
[6 empty] | Motor burnt | 4 |  |  |  |  | Earthing Pit PM | NA
[12 empty] | Capacitor | Ok
[11 empty] | 2016-03-01 | Maintenance free battery | 0
[12 empty] | Distilled water battery | 10*2times
[12 empty] | Emergency Light trial | Ok 30.3.16
[12 empty] | Transformer PM | NA
[12 empty] | Earthing Pit PM | Ok 18.3.16
Note on E5: admin: 01G4B(standby motor under maintenenc); TF4-32C
Note on M5: admin: 92 thermography points coverd internally by sal & External thermography conducted on 29.5.15 by M/S Microaids
Note on E7: admin: P-308A;P-411B;P-422D-change over not given of standby motor
Note on M7: admin: Schedule is in Sept-15
Note on M9: admin: Schedule is in Sept-15
Note on M11: admin: Schedule is in Sept-15
Note on E15: admin: FD-309 motor
Note on E17: Pending motors 03G6A,P-33A,P-202,P-456A
Note on E19: Pending motors 03G6A,P-33A,P-202,P-456A from previous month completed
Note on M19: admin: K3 panel MCCB contact area cleaned and PCC R phase contact cleaned. 9/12/15 by SAL
Note on E23: admin: P-456A pending
Note on I33: admin: 01G17 and C-403
Note on I49: admin: P-705A motor bearing replacement

## from 2016-17
Month | Equipment | Shutdown | Planned | Completed | Slippage | Condition Monitoring of Bearing |  |  | Month | Equipment | Equipment Covered | Month | Equipment | Nos/status
2016-04-14 | Motor |  | 113 | 112 | 1 | 2016-04-14 | Bearing Cm | 51 | 2016-04-14 | Thermography | 0 | 2016-04-14 | Maintenance free battery | 14
| Panel |  | 25 | 25 | 0 |  | Bearing Replacement | 10 |  | Greasing | 0 |  | Distilled water battery | 9*2times
2016-05-14 | Motor |  | 107 | 107 | 0 |  | Planned for bearing replacement | 0 | 2016-05-14 | Thermography | 1 |  | Emergency Light trial | OK taken on 25.4.16
| Panel |  | 29 | 29 | 0 |  | Motor burnt | 2 |  | Greasing | 0 | 2016-05-14 | Transformer PM | 7 done by AVV on 3.5.16
2016-06-14 | Motor |  | 103 | 97 | 6 | 2016-05-14 | Bearing Cm | 49 | 2016-06-14 | Thermography | 100 |  | Earthing Pit PM | NA
| Panel |  | 29 | 29 | 0 |  | Bearing Replacement | 5 |  | Greasing | 16 |  | Emergency Light trial | 30.5.16
2016-07-14 | Motor |  | 96 | 89 | 7 |  | Planned for bearing replacement | 2 | 2016-07-14 | Thermography |  |  | Distilled water battery | 9*2times
| Panel |  | 25 | 25 | 0 |  | Motor burnt | 2 |  | Greasing |  | 2016-06-14 | Maintenance free battery | NA
2016-08-14 | Motor | 52 | 108 | 107 | 3 | 2016-06-14 | Bearing Cm | 187 | 2016-08-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 0 | 25 | 25 | 0 |  | Bearing Replacement | 5 |  | Greasing | 0 |  | Emergency Light trial | 1.6.16
2016-09-14 | Motor | 10 | 106 | 98 | 8 |  | Planned for bearing replacement | 4 | 2016-09-14 | Thermography | 0 |  | fire alarm testing | 21 & 22.6.16
| Panel | 1 | 24 | 24 | 0 |  | Motor burnt | 0 |  | Greasing | 0 | 2016-07-14 | Maintenance free battery
2016-10-14 | Motor | 6 | 115 | 109 | 6 | 2016-07-14 | Bearing Cm |  | 2016-10-14 | Thermography | 86 |  | Distilled water battery
| Panel | 0 | 24 | 24 | 0 |  | Bearing Replacement |  |  | Greasing | 0 |  | Emergency Light trial
2016-11-14 | Motor | 19 | 113 | 98 | 15 |  | Planned for bearing replacement |  | 2016-11-14 | Thermography | 0 |  | fire alarm testing
| Panel | 3 | 29 | 29 | 0 |  | Motor burnt |  |  | Greasing | 44 | 2016-08-14 | Maintenance free battery | NA
2016-12-14 | Motor | 0 | 123 | 119 | 4 | 2016-08-14 | Bearing Cm | 10 | 2016-12-14 | Thermography | 61 |  | Distilled water battery | 9*2times
| Panel | 0 | 21 | 21 | 0 |  | Bearing Replacement | 7 |  | Greasing | 22 |  | Emergency Light trial | 17.08.2016
2017-01-14 | Motor | 0 | 104 | 104 | 0 |  | Planned for bearing replacement | 0 | 2017-01-14 | Thermography | 19 |  | fire alarm testing | NA
| Panel | 0 | 36 | 36 | 0 |  | Motor burnt | 1 |  | Greasing | 26 | 2016-09-01 | Maintenance free battery | NA
2017-02-14 | Motor | 0 | 96 | 96 | 0 | 2016-09-14 | Bearing Cm | 56 | 2017-02-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 0 | 30 | 30 | 0 |  | Bearing Replacement | 8 |  | Greasing | 0 |  | Emergency Light trial | 22.09.16/ 23.09.16
2017-03-14 | Motor | 0 | 97 | 96 | 1 |  | Planned for bearing replacement | 0 | 2017-03-14 | Thermography | 83 |  | fire alarm testing | NA
| Panel | 0 | 29 | 29 | 0 |  | Motor burnt | 1 |  | Greasing | 0 | 2016-10-01 | Maintenance free battery | 15
[6 empty] | 2016-10-14 | Bearing Cm | 4 |  |  |  |  | Distilled water battery | 9*2times
|  |  | 1281 | 1232 | 96.1749 |  | Bearing Replacement | 7 |  |  |  |  | Emergency Light trial | 17.10.16
|  |  | 326 | 326 | 100 |  | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[5 empty] | 98.0874 |  | Motor burnt | 2 |  |  |  | 2016-11-01 | Maintenance free battery | NA
[6 empty] | 2016-11-14 | Bearing Cm | 140 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 12 |  |  |  |  | Emergency Light trial | -
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 3 |  |  |  | 2016-12-01 | Maintenance free battery | NA
[6 empty] | 2016-12-14 | Bearing Cm | 4 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 6 |  |  |  |  | Emergency Light trial | 01.12.16
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | 12.12.16/ 13.12.16
[7 empty] | Motor burnt | 1 |  |  |  | 2017-01-01 | Maintenance free battery | NA
[6 empty] | 2017-01-14 | Bearing Cm | 218 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 8 |  |  |  |  | Emergency Light trial | 11.01.17
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 1 |  |  |  | 2017-02-01 | Maintenance free battery | NA
[6 empty] | 2017-02-14 | Bearing Cm | 0 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 10 |  |  |  |  | Emergency Light trial | 11.01.17
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 4 |  |  |  | 2017-03-01 | Maintenance free battery | NA
[6 empty] | 2017-03-14 | Bearing Cm | 0 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 10 |  |  |  |  | Emergency Light trial | 14.03.17
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 2
| Shutdown Motor |  |  | 22
Note on F2: admin: 03G3A Pending
Note on N4: admin: 02G1 bypass contact cleaned
Note on J9: 20P03B & 02G1
Note on F10: AUG: Pre. Month: VP-351A P-354B P-308A
Note on F12: SEP: P-964,513B,819B, VP-351B, 14B, D-1-2, CT-903B Pre. Month: P-354B
Note on F13: Stability Chamber QC
Note on F14: OCT-16: 01G13A, P-802B, P-364A, P-1013C PRE. MONTH: D-1-2, CTF-903B
Note on F16: 01G16A,P-966, P-202,VPX-601B, CTF-1,P-362C, P-657A, P-9002B, P-808B, P-453B, P-351B, 354A, 355A, 356A,361B
Note on C17: CPP PMCC 11 KV HT Panel 10 MVA, 22 KV HT Panel
Note on F18: P-710B, P-652, P-654, P-655
Note on N18: admin: K3 panel MCCB contact area cleaned and PCC R phase contact cleaned. 9/12/15 by SAL
Note on J21: P-7102
Note on F24: P-513B
Note on J25: P-7100A
Note on J29: P-31B P-1001B
Note on J32: admin: 01G17 and C-403
Note on J33: 06G1A VP-7103B P-7100A
Note on J37: P-7120
Note on J41: Pestillator Forklift Stering Motor
Note on J45: 01G19B P-1016B Degasser Blower ETP Submersible Pump 07G7B
Note on J49: P-3B P-7104B

## Bearing failure (hidden)
Sr.No. | Date | Eqpt.Name | Tag No. | Kw/Rpm | Bearing No. | Reported By | Work Done By | Location
2014-05-13
1 | 06.05.14 | CW supply Pump for Splitting & SW | P-9002A | 90/1400 | 6317/6316 C3 |  | CPP/RANA | CGS
2 | 07.05.14 | Distillate transfer pump | P-514B | 7.5/2900 | 6208ZZC3 |  | GTC | DFA
3 | 13.05.14 | Residue transfer pump-1 | P-407A | 9.3/2940 | 6309C3 |  | CPP
4 | 18.05.14 | Vaccum pump | P-522 | 5.5/1440 | 6308/6208 ZZ | DILIP/AVV
5 | 25.05.14 | K-3 Reboiler circulation pump | P-29B | 15 | 6309C3
2014-06-13
1 | 05.06.14 | Circulation pump for 01D2 | 01G2A | 11/2945' | 6312/6311ZZC3 | SAL | RSM/RNP | FAP
2 | 05.06.14 | Bottom circulation pump | P-511B | 15/1450 | 6309/6209ZZC3 | RNP/DLK | RNP/DLK | DFA
3 | 10.06.14 | Circulation pump for 01D4 | 01G4A | 55/2950 | 6315C3/6215C3 |  | RSM/AVV | FAP
4 | 12.06.14 | Atlas copco air compressor | 06G1D | 75/2975 | NU215ECP/6215K4VT269 |  | DLK/Aircom | Utility
5 | 14.06.14 | Oil fat trap pump | P-816B | 3.7/2900 | 6206ZZC3/6205ZZC3 |  | RSM/AVV | New TF
6 | 20.06.14 | Hotwell Pump | P-206.3/D-1-1 | 30/2940 | 6312zz/6311zz |  | RSG | Noodle plant ,used for D-1-1
7 | 23.06.14 | Hot Well Pump-1 - Loop Reactor | P-802A | 15/2910 | 6209ZZC3 | RSM | RSG | Loop Reactor
8 | 30.06.14 | pump for cooling water return-3 | C-403 | 11/2935' | 6309 ZZc3/6309ZZC3 |  | CPP/SKP | Flaker top
9 | 29.06.14 | Feed Pump Pestillator-1 | P-651A | 15/2940 | 6309C3 |  | AVV/SKP | GDP GR Floor
2014-07-13
1 | 01.07.14 | Tempered water circulation pump | 01G14B | 75/1480 | 6317C3/6316C3 |  | RSM/RANA | Pestillator terrace spare motor for 01G14B
2 | 01.07.14 | Hydrocarbon transfer pump | 01G20 | 3.7/2885 | 6308ZZC3/6307ZZC3 | SKP | Rana/CPP | FAP
3 | 9.7.14 | Linde FD fan | F-102 | 7.5/2885 | 6308ZZC3/6307ZZC3 | CM | SAL | Linde First floor
4 | 11.7.14 | Flaker cooling tower | C-402 | 11/2935 | 6309ZZC3 | AVV | SAL/SKP | Flaker top
5 | 10.07.14 | BFW | 07U1G2B | 7.5/2910 | 7308BE2RS/6206ZZRC3 | CM |  | Old boiler
6 | 16.7.14 | Hotwell Pump | D-1-2 | 30/2930 | 6313C3 | CM | SAL | DFA 3rd floor
7 | 18.7.14 | Linde ID fan | F-101 | 30/2945 | 6312C3/6212C3 | CPP | SAL/RANA | Lind ID Fan
8 | 19.7.14 | CPP CT fan-1 | P-1016A | 15/1450 | 6309C3 | RNP | RNP | CPP Cooling tower CT Fan
9 | 14.07.14 | PITCH PUMP | P-7110B | 3.7 | 6205ZZC3/6206ZZC3 | SKP | SKP/AVV | GDP ground floor
10 | 25.07.14 | Effluent transfer pump | 05U1G8 | 1.5/900 | 62052ZZC3 | RSM/SKP | TOM | Old boiler terrace
11 | 30.7.14 | D-20 DM water V-303 | P-34B | 7.5/2850 | 6308ZZC3/6307ZZC3 | SAL |  | New boiler terrace
2014-08-13
12 | 13.08.14 | TANK FORM FEED PUMP | P-7100A | 9.3/2860 | 6308ZZC3/6307ZZC3 | RSG/RSM |  | New TF
13 | 16.08.14 | Circulation pump for 01D3 | 01G3A | 30/2955 | 6312C3/5212C3 | CPP | RNP/RSM | FAP
14 | 22.08.14 | CPP CT fan-2 | P-1016B | 15/1450 | 6309C3 | CM | RSM/GTC | CPP Cooling tower CT Fan
2014-10-14
1 | 05.10.14 | C401 bottom transfer | P-424B | 7.5/2935 | 6208ZZC3 | RSM/AVV | RSM/CPP | DFA
2 | 08.10.14 | Hotwell pump Sec-3 | 03G18A | 15/2920 | 6209ZZC3 |  | CPP | Alcohol
3 | 09.10.14 | Bioler feed water pump 3TPH | 07U1G2A | 7.5/2910 | 6308ZZC3/6206ZZC3 |  | SAL | Utility
4 | 09.10.14 | Bioler feed water pump 3TPH | 07U1G2B | 7.5/2910 | 6308ZZC3/6206ZZC3 |  | SAL | Utility
5 | 09.10.14 | Froced draft fan bioler 3TPH | 07U1G1B | 11/2910' | 6209ZZC3 |  | RNP | Utility
6 | 07.10.14 | Terpered cooling water III pump | 01G16A | 55/1400 | 6215C3/6315C3 |  | SAL | Alcohol
7 | 20.10.14 | L/E or Refulx pump of C401 | P-421B | 5.5/2932 | 6208ZZC3 | RSG/DLK |  | DFA
8 | 21.10.14 | Oil dhakka circulation pump | P-824 | 22/2930 | 6310C3
9 | 23.10.14 | Inline pump for thermal oil | 03G4A | 11/1450 | 6309ZZC3/6308ZZC3 | CPP | RSG | Alcohol
2014-11-14
1 | 5.11.14 | Air compressor | 06G1G | 75/2430 | NU215ECP/6215K4VT269 | CM | RSM/Airkom vendor | DFA Air compressor house
2 | 7.11.14 | MCT blitcher |  | 3.7 | 6207ZZC3/6208ZZC3 |  | SAL | DFA first floor
3 | 8.11.14 | Thermic [pump | P-7122 | 7.5/1440 | 6308ZZC3/6307ZZC3 | SAL/CPP | AVV/RSM | GDP
4 | 13.11.14 | BFW | 07U1G3B | 7.5/2930 | 6308ZZC3/6206ZZC3 | CM | rsm/sal | Old boiler
5 | 15.11.14 | BFW | 07U1G3A | 7.5/2930 | 6308ZZC3/6206ZZC3 | CM | avvv/rsm | Old boiler
6 | 22.11.14 | Chilling Inlet Motor | P-962 | 18.5/2920 | 6309ZZC3/6209ZZC3 | SKP/RNP | rsm | Pastillator
7 | 24.11.14 | Air compressor | 06G1G | 75/2430 | NU215ECP/6215K4VT269 | avv/skp |  | DFA Air compressor house
2014-12-14
1 | 06.12.14 | CONDENSATE PUMP | 07G7B |  | 6203ZZ | avv/rnp | rnp | Near 7P-45C heater
2 | 14.12.14 | Hot oil circulation pump-1 | P-311A | 15/1475 | 6309C3 | CPP/RNP | RSM/AVV/RANA | DFA
3 | 20.12.14 | Direct cooling water return pump-2 | P-422B | 22/2940 |  | AVV/RSM |  | DFA 2nd Floor
4 | 28.12.14 | HOT WATER PUMP-A | P-1015A | 18.5/2930 | 6309ZZC3/6209ZZC3 | RNP/DLK |  | CPP CT fan
5 | 29.12.14 | Hotwell Pump | P-360A | 30/2830 | 6312ZZC3/6311ZZC3 | rnp/skp | RSG | Jutasama 3rd floor
6 | 31.12.14 | Agitator for 08T9A | 08N14A | 4/1440 | 6205ZZC3/6206ZZC3 | sal | sal | Old TF
7 | 31.13.14 | Agitator for 08T3B | 08N18B | 2.2/1420 | 6205ZZC3/6206ZZC4 | sal | sal | OLD TF
2015-01-14
1 | 7.1.15 | Cooling water pump | 05G9D | 30/2955 | 6312/6212C3 |  | sal/cpp | Old boiler
2 | 9.1.15 | ETP Pit Pump | P-913B | 7.5/2850 | 6308ZZC3/6307ZZC3 | sal |  | Old boiler
3 | 10.1.15 | Feed Pump | P-651A | 15/2940 | 6309C3 | sal | sal | GDU postcon
4 | 12.1.15 | B/P Pump K3' | P-355A | 11/2940 | 6309C3 | sal | sal | Jutasama 1st floor
5 | 13.1.15 | Cooling water pump | 05G9G | 30/2955 | 6312ZZC3 | rnp | sal | Old boiler
6 | 13.1.15 | Dehydrator circulation Pump | P-351B | 22/2944 | 6310C3 | sal | sal | Jutasama 4th floor
7 | 14.1.15 |  | P-7106 | 5.5/2920 | 6208ZZC3 | cpp/skp | sal | GDP gnd floor
8 | 16.1.15 | Feed pump Jutasama | P-104D | 30/2930 | 6312C3/6312C3 | sal | sal | New TF
9 | 21.1.15 | Chilling Inlet Motor | P-962 | 18.5/2920 | 6309ZZC3/6209ZZC3 | gtc | sal | Pastillator
10 | 25.1.15 | Blower | BDG-2 | 0.55/2840 | 6202ZZC3 | cpp/avv |  | Old boiler
11 | 28.1.15 | cooling water pump -1 | C-301 | 11/2935 | 6309ZZC3 | rsg/avv | rnp | Flaker
2015-02-14
1 | 7.02.15 |  | 07U2G1B | 110/1400 | 6319C3/6316C3 | cpp/skp | sal/rnp | TP-45
2 | 8.2.15 |  | P-36B | 22/2940 | 6210C3/6210C3 | avv/skp | cpp/rsm | DFA 2nd Floor
3 | 8.2.15 |  | P-27A | 15/1460 | 6309ZZC3 | avv/skp | cpp/rsg | DFA 6th floor
4 | 7.2.15 |  | 02G8A | 37kw | 6312C3/6212C3 | avv/skp | cpp/rsg | FAP ground floor
5 | 9.2.15 |  | P-30B | 7.5/2900 | 6208ZZC3/6305ZZC3 | avv/skp | rsg/cpp | DFA ground floor
6 | 9.2.15 |  | P-33A | 9.3/1450 | 6309C3/6308C3 | avv/skp | cpp | DFA
7 | 9.2.15 |  | D-1-1 | 30/2940 | 6312ZZC3/6311ZZC3 | gtc | rsm/sal | DFA 3rd floor
8 | 10.2.15 |  | Filter press-A | 1.5/1415 | 6205ZZC3 | avv/dlk | rsm | FAP ground floor
9 | 11.2.15 | Blower | BDG-2 | 0.55/2840 | 6202ZZC3 | gtc | rnp/rsg | Old boiler
10 | 16.2.15 |  | 07U1G1A | 18.5/2910 | 6209C3 | cpp |  | SM-50 blower
11 | 16.2.15 |  | 06G1G exhaust blower motor | 2/920 | 6007ZZ/6007ZZ | airkom rahul | sal | DFA boiler house 75 kw compressor
12 | 14.2.15 |  | P-962 | 18.5/2920 | 6309ZZC3/6209ZZC3 |  | rsm | Pastillator ground floor
13 | 21.2.15 |  | P-318A | 5.5/2880 | 6205ZZC3/6306ZZC3 | sal | rsg/rana | DFA
14 | 25.2.15 |  | 03G1B | 55/2960 | 6315C3/6215C3 | rnp | rnp/rana | FAP 1st floor
15 | 25.2.15 |  | P-7120 | 3.7/2930 | 6306ZZC3/6206ZZC3 | cpp | cpp | GDP
16 | 28.5.15 |  | 05G9E | 30/2955 | 6312C3 |  | rsm/rnp/cpp | Old boiler
2015-03-14
1 | 28.2.15 |  | 02G5AG1 | 0.75/910 | 6205ZZC3 | CM | rsm | FAP
2 | 2.03.2015 |  | P-208A | 7.5/2900 | 6305ZZC3/6208ZZC3 | avv/rsg | avv/cpp | DFA
3 | 3.3.15 |  | TF-4-32B | 3.7/2865 | 6206ZZC3/6205ZZC3 | rsm |  | Flaker backside
4 | 26.3.15 |  | 03G3A | 37/2955 | 6312C3/6313C3 | rsm | sal | FAP ground floor
2015-04-14
1 | 9.4.15 |  | P-962 | 18.5/2920 | 6309ZZC3/6309ZZC3 | gtc | tom | Pastillator ground floor
2 | 11.4.15 |  | 07U2G1A | 110/1485 | 6319C3/6316C3 | rnp |  | TP-45 section
3 | 13.4.15 |  | 02G1 | 435/12pole | 6326MC3/6326MC3 | rnp/cpp | Om Sai | H2 compressor house
4 | 25.4.15 |  | P-307B | 15/1450 | 6309C3/6309C3 | gtc |  | DFA Gnd Floor
2015-05-14
1 | 4.5.15 |  | P-36A | 22/2930 | 6310ZZC3/6310ZZC3 |  | rnp | DFA
2 | 7.5.15 |  | P-7122 | 7.5/1440 | 63085ZZC3/6307ZZC3 | rsm/rnp |  | GDP
3 | 9.5.15 |  | 08N14A | 4/1440 | 6206ZZC3/6205ZZC3 | avv/skp | sal | Old Tankfarm
4 | 9.5.15 |  | P-456B | 30/2955 | 6312C3/6212C3 |  |  | Jutasama 3rd floor
5 | 11.5.15 |  | 08N16A | 1.5/1420 |  |  | Sanjayraj | Old Tankfarm
6 | 19.5.15 |  | MCT Bleacher | 4/1440 | 6208ZZC3/6207ZZC3
7 | 21.5.15 |  | Canteen Grinder Mixer | 0.75/90 |  |  | rnp | Canteen A
8 | 26.5.15 |  | P-1012C | 30/2940 | 6311ZZC3/6312ZZC3 | sal | rsm/sal | CPP Terrace
9 | 27.5.15 |  | P-1012A | 30/2940 | 6311ZZC3/6312ZZC3 | sal | rsm | CPP Terrace
10 | 27.5.15 |  | Garden Grass Cutter |  | 6204ZZC3
11 | 30.5.15 |  | P-306B | 11/2840 | 6309ZZC3/6309ZZC3 | skp | sanjayraj | DFA 1st floor
12 | 30.5.15 |  | 23P2 | 15/2940 | 6309C3/6309C3 | sal | sanjayraj | CGS Ground floor
2015-06-14
| 1.06.15 |  | P-30B | 7.5/2900 | 6208ZZC3/6305ZZC3 |  |  | DFA Gnd Floor
| 3.6.15 |  | VP-601A | 11/1400 | 6309ZZC3/6309ZZC3 | avv | rsm/sal
| 5.6.15 |  | P-306B | 11/2940 | 6309ZZC3/6309ZZC3 |  | sal
| 24.6.15 |  | Sm-50 blower | 18.5/2900 | 6309ZZC3/6308ZZC3 |  |  | Old boiler
|  |  | 02G3 | 330kw
| 29.6.15 |  | 05G11B | 11/2pole | 6309ZZC3/6209ZZC3
| 29.6.15 |  | 09U1G15B
2015-07-14
| 6.7.15 |  | P-322A | 18.5/1475 | 6310ZZC3/6310ZZC3 |  | rsg | DFA 2nd Floor
| 7.7.15 |  | P-412B | 11/2930 | 6309ZZC3/6209ZZC3 | gtc |  | DFA gnd floor
| 7.7.15 |  | C-303 | 11/2935 | 6309/6309 | sal |  | FALKER gnd floor
| 8.7.15 |  | 09U1G20 | 11/2920 | 6309ZZC3/6209ZZC3 | avv |  | ETP gnd floor
| 10.7.15 |  | TF-4-32C | 5.5/2980 |  |  |  | Flaker gnd floor
| 11.7.15 |  | P-1012A | 30/2940 | 6311ZZC3/6312ZZC3 | avv |  | CPP 3rd floor
| 14.7.15 |  | P-819B | 5.5/2870 |  |  |  | New TF
| 15.7.15 |  | 03G18A | 15/2920 |  |  |  | FAP 2nd floor
| 17.7.15 |  | 01G11A |  |  |  |  | Stripper gnd floor
| 23.7.15 |  | P-819A | 5.5/2870 |  | CM |  | New TF
| 22.7.15 |  | 01G6A | 7.5/1455 | 639ZZ/6308ZZ |  |  | FAP gnd floor
2015-08-14
| 6.8.15 |  | P-8001A | 5.5/2920 |  | GTC |  | DFA
| 26.8.15 |  | 02G3 | 330/16pole | 6326MC3 | CM | Farhan Electrical | H2 compressor house
| 26.8.15 |  | P-1016A | 15/1450 | 6309ZZC3 | CM | Sanjayraj | CPP Cooling tower CT Fan
| 27.8.15 |  | P-1016B | 15/1450 | 6309ZZC3 | CM | Sanjayraj | CPP Cooling tower CT Fan
| 31.8.15 |  | 02G3G1 | 1.1/1425 | 6206ZZC3 | CM | Ramesh | 02G3 Lub oil pump
2015-09-14
| 3.9.15 |  | 01G12B | 11/1450 | 6308ZZC3/6309ZZC3 | CM | Sal | FAP
| 5.9.15 |  | P-34A | 7.5/2850 | 6308ZZC3/6307ZZC3 |  |  | DFA
| 5.9.15 |  | 01G5B | 30/2955 | 6312C3/6212C3 | Cm | gtc/rnp | FAP
| 12.9.15 |  | P-710B | 5.5/1450 | 6308ZZC3/6208ZZC3 |  | rsg | Loop Reactor
| 16.9.15 |  | CGS -Agitator motor | 0.75/315 |  |  | rsg/cpp | CGS
2015-10-14
| 1.10.15 |  | 01G1A | 55/2950 | 6315C3/6215C3 | CM | rnp | FAP ground floor
| 2.10.15 |  | 03G17B |  | 6311ZZC3/6312ZZC3 |  | cpp/skp
| 10.10.15 |  | 06G1A | 90/4pole |  | CM
| 10.10.15 | Dozing pump | 10U2G1 |  | 6202ZZ/6202ZZ |  | rnp
| 14.10.15 |  | P-422B | 22/2940 |  |  |  | DFA 2nd floor
| 15.10.15 |  | P-7117 | 5.5/2905 | 6206ZZC3/6206ZZC3 | gtc | sal | GDP Ground Floor
| 24.10.15 |  | BFW-1 IAEC Boiler | 18.5/2920 | 6309C3/6309C3 | rsg | GTC | New boiler
| 25.10.15 |  | P-366 |  | 6205ZZC3/6205ZZC3 |  |  | DFA 7th floor
2015-11-14
| 4.11.15 |  | P-150.3 | 3.7/2900 | 6306ZZC3/6306ZZC3 | rnp |  | CGS Ground floor
|  |  | P-515B | 18.5/2920 | 6309ZZC3/6209ZZC3 |  |  | DFA
| 16.11.15 |  | 03G18B |  | 6309ZZC3 |  | sal
| 19.11.15 |  | P-431B | 18.5/2910 | 6209ZZC3 | rnp | rnp | DFA 2nd Floor
| 20.11.15 |  | Single phase motor dosa mixer |  |  |  |  | Canteen A
| 20.11.15 |  | CGS filter press hydraulic motor | 2.2/1415 | 6205ZZC3/6206ZZC3 | rsm | rsm | CGS Ground floor
| 20.11.15 |  | TF-4/32C | 5.5/2880 | 6306ZZC3/6205ZZC3 | gtc |  | TF-4
| 25.11.15 |  | New boiler pit pump | 2.2/2880 | 6205ZZC3 |  |  | New boiler
2015-12-14
| 1.12.15 |  | Vibro Feeder | 0.37 | Roller Bearing | CHP operator | Sanjay Raj | CHP plant
| 2.12.15 |  | 01G17A | 1.5/2825 | 6205ZZC3 | RSG | SAL | Alcohol 3rd floor
| 4.12.15 |  | C-403 | 1.5/2826 | 6309ZZC3/6309ZZC3 | CPP | CPP | Flaker
| 19.11.15 |  | P-655 | 22/2910 | 6310ZZC3 | CM | SAL | Alfa Postcon
| 20.11.15 |  | 01G19B | 15/2920 | 6309ZZC3/6209ZZC3 | CM | SAL | Stipper ground floor
| 20.11.15 |  | P-3A | 3.7/2930 | 6206ZZC3/6306ZZC3 | CM | SAL | K-3 2nd floor
| 20.11.15 |  | Spare | 30 | 6313ZZC3 |  | DLK | Spare
| 25.11.15 |  | Spare | 5.5/2835 | 6306ZZC3 |  | RSG
2016-01-01
| 9.1.16 |  | BDG-1 | 0.37 |  |  | RSM | old Boiler
| 15.1.16 |  | P-420 | 1.5 |  | CM | RSM | MCC 103
| 16.1.16 |  | 05G9G | 30 | 6312ZZC3/6312ZZC3 | CM | RSM | old Boiler
| 12.1.16 |  | C-402 | 11 | Planned for next month
| 20.1.16 |  | VP-651B | 15 | 6309ZZC3/6209ZZC3 | SAL | SAL | Postcon
| 27.1.16 |  | Spare motor | 15 | 6309ZZC3/6209ZZC3 |  | SAL
2016-02-02
| 2.2.16 |  | P-309B | 2.2 | 6205ZZC3/6205ZZC3 | RSG | RSG | DFA Ground Floor
| 2.2.16 |  | Spare Motor | 2.2 | 6205ZZC3/6205ZZC4 | RSG | RSG | DFA Ground Floor
| 7.2.16 |  | P-307A | 15 | 6309C3/6309C3 | GTC | SAL | DFA Ground Floor
| 22.2.16 |  | P-802A | 15 | 6209ZZC3/6209ZZC3 | RSG | RSM/GTC | Loop Reactor Ground
| 25.2.16 |  | 03G3A | 11 | 6308ZZC3/6309ZZC3 | CM | SAL
| 25.2.16 |  | 05G13 | 30 | 6312ZZC3/6212ZZC3 | RSM | RSM | Water Tank Area Boiler
| 29.2.16 |  | 03G1B | 55 | 6315C3/ 6215C3 | CPP | CPP
2016-03-02
| 12.03.16 |  | P-320B | 22 | 6210C3/6210C3 | CM | SAL | DFA Ground Floor
| 15.3.16 |  | P-651A | 15 | 63090C3/6309C3 | GTC | SAL | DFA Ground Floor
| 16.3.16 |  | DAA | 7.5 | 6208ZZC3/6208ZZC3 | CM | SAL | ETP
| 16.3.16 |  | DAF | 7.5 | 6208ZZC3/6208ZZC3 | CM | SAL | ETP
| 17.3.16 |  | P-802B | 15 | 6209ZZC3/6309ZZC3 | CM | RNP | Loop Reactor Ground
| 25.3.16 |  | 05G9F | 30 | 6312ZZC3/6212ZZC3 | CM | SAL | Old Boiler Utility ground floor
| 31.3.16 |  | P-1050A2 | 150 | 6319C3 ( DE Side) only | CM | SAL/RANA | Coal heater ground floor
2016-04-02
| 2.4.16 |  | 06G1G Dryer Motor | 0.55 | 6002ZZ/6002ZZ | Vendor | SAL | DFA Air Compressor
| 22.4.16 |  | 06G1D | 75 | NU215ECP/ 6215 /C4VT269 | CM | Sanjay Raj | Air Compressor
| 16.3.16 |  | 20P07B | 15 | 6309ZZC3 / 6209ZZC3 | CM | SAL | ETP
2016-05-02
| 1.5.16 |  | 03G17A | 22 | 6312ZZC3/6211ZZC3 | CM | RNP | alochol
| 20.5.16 |  | 20P03A | 110 | 6316C3/6319C3 | Varun | SAL/RNP | Fatty Acid
| 22.5.16 |  | 05G3C | 3.7/2900 | 6205ZZC3/6206ZZC3 | CPP | SAL/RNP | Utility
| 22.5.16 |  | 910B | 7.5/2850 | 6308ZZC3/6307ZZC3 | CM | AVV/RSG | Fatty Acid
| 13.5.16 |  | P - 1012A | 30/2900 | 6311ZZC3/6312ZZC3 | CM | RNP | CPP
2016-06-16
| 20.6.16 |  | P-1050B1 |  | BEARING CLEANED | CM | RSM/AVV
| 22.6.16 |  | P-513B |  | 6312ZZ,6212ZZC3 | CM | RNP/GTC | K4
| 25.6.16 |  | P-802C | 18.5/2930 | 6312ZZ,6212ZZC3 | CM | SAL/BHP | TF
| 25.6.16 |  | P-705B | 55/989 | 6318C3 | SPARE | SAL | Loop Reactor Ground
2016-07-01
2016-08-01
1 | 01.08.16 |  | P-516A | 2.2/2900 | 6205ZZ/ 6205ZZ | CM | RSG/SAL | K4
2 | 11.08.16 |  | 09U1G21 | 5.5/2900 | 6208ZZ/6208ZZ | CM | RSM/DLK | ETP
3 | 13.08.16 |  | 10G02 | 9.3/1400 | 6309ZZ/6209ZZ | CM | CPP/DLK | CALORIC
4 | 13.08.16 |  | BL-1301 | 3.7/1400 | - | CM | CPP/DLK | SYNDENT
5 | 17.08.16 |  | 01G5B | 30/2900 | 6312ZZ/ 6212ZZ | CM | SAL/BHP | FAP GF
6 | 24.08.16 |  | FLACKER MOTOR-SION | 22/2900 | 6210ZZ/ 6210ZZ | SION | BHIM | SION
7 | 24.08.16 |  | GDP MOTOR-SION | 11./2900 | 6309ZZ/6209ZZ | SION | RNP/CPP | SION
8 | 28.08.16 |  | DEGASER BLOWER | 0.37/2900 | 6203ZZ/ 6203ZZ | UTILITY | - | UTILITY
2016-09-01
1 | 11.09.16 |  | Utility Blower | 0.75/1440 | 6204 C3/ 6204 C3 | UTILITY | BHIM | UTILITY
2 | 13.09.16 | High Pressure Fat / Water Feed Pump | P-602B | 2.2/ 2900 | 6205ZZ/ 6205ZZ | RSM | SAL/AVV | Precon
3 | 15.09.16 | Raw water pump-2 | 20P07B | 15/2900 | 6309 ZZ C3/ 6309 ZZ C3 | CM | RSM | RAW WATER
4 | 19.09.16 | Linde ID fan | F-101 | 30/2900 | 6312 ZZ C3/ 6212 ZZ C3 | CM | SAL/RNP | LINDE
5 | 17.09.16 | K-3 bottom product transferring pump | P-30A | 15/2900 | 6309 ZZ C3/ 6309 ZZ C3 | CM | BHIM | K3
6 | 22.09.16 | D-10 to K-3 | P-4A | 22/2900 | 6310 ZZ C3/6310 ZZ C3 | CM | RSG/DLK | DFA
7 | 21.09.16 | Linde FD fan | F-102 | 7.5/2900 | 6307 ZZ C3/ 6308 ZZ C3 | CM | SAL/ RSG | LINDE
8 | 29.09.16 | Condensate transfer pump-1 | P-816A | 1.1/2900 | 6204 ZZ/ 6204 ZZ | CPP | RNP/AVV | TANKFARM
2016-10-01
1 | 03.10.16 | Water Charge Pump. | P-203 | 22/1440 | 6311 ZZ C3/ 6312 ZZC3 | CM | SAL | DFA
2 | 25.10.16 | Hotwell Pump | P-360B | 37/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | AVV/ SAL | JUTASAMA
3 | 08.10.16 | CHILLED WATER PUMP | P-304 | 11./2900 | 6309ZZ/6209ZZ | CM | RSG/GTC | FLACKER
4 | 27.10.16 | AUX.AIR FAN B | P-1001B | 2.2/2900 | 6205 ZZ/ 6205 ZZ | CPP | SAL | CPP
5 | 27.10.16 | AUX.AIR FAN A | P-1001A | 2.2/2900 | 6205 ZZ/ 6205 ZZ | CPP | AVV/GTC | CPP
6 | 27.10.16 | HOT WATER PUMP-2 | P-1015B | 11./2900 | 6309ZZ/6209ZZ | CPP | SAL/RANA | CPP
6 | 29.10.16 | CW supply Pump for Splitting & SW | P-9002B | 80/1440 | 6316 C3/ 6316 C3 | AVV | SAL/RANA | SPLITTING
2016-11-01
1 | 05.11.16 | K-3 Reboiler thermic fluid circulation pump | P-36A | 22/2900 | 6310ZZ C3/ 6310 ZZ C3 | SAL | SAL | DFA
2 | 12.11.16 | Clean CW Pump -Precon & Postcon | P-364A | 75/1450 | 6317 C3/ 6317 C3 | CM | CPP/RANA | JUTASAMA
3 | 14.11.16 | PESTILLATOR AHU | AHU Motor | 5.5/2900 | 6308 ZZ C3/ 6308 ZZ C3 | TOM | Sanjayraj | Pestillator
4 | 19.11.16 | Forklift-2 | Stering Motor | 0.65/2100 | 6006 ZZ/ 6202 ZZ | RSM | Sanjayraj | Pestillator
5 | 16.11.16 | Terpered cooling water I pump | 05G10B | 90/2900 | 6316 C3/ 6319C3 | CM | CPP/ RSG | Acid Stripper
6 | 23.11.16 | DM water pump | P-363A | 11/2900. | 6209 ZZ C3/ 6309 ZZ C3 | CM | CPP | JUTASAMA
7 | 25.11.16 | Circulation pump | 03G15B | 18.5/2900 | 6309 ZZ C3/ 6310 ZZ C3 | BHP | RNP | FAP GF
8 | 28.11.16 | COOLING TOWER PUMP-A | P-1012A | 30/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | RSM | CPP
9 | 28.11.16 | COOLING TOWER PUMP-B | P-1012B | 30/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | RSM | CPP
10 | 29.11.16 | COOLING TOWER PUMP-C | P-1012C | 30/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | RSM | CPP
11 | 29.11.16 | COOLING WATER GT PUMP-B | P-1017B | 7.5/2900 | 6307 ZZ C3/ 6308 ZZ C3 | CM | RSG | CPP
12 | 29.11.16 | SAF GD-03 | P-1008 | 1.5/2900 | 6205 ZZ/ 6205 ZZ | CM | RSM | CPP
2016-12-01
1 | 01.12.16 | L.P.condensate pump | 07G1B | 1.5/ 2900 | 6203 ZZ C3/ 6203 ZZ C3 | AVV | RSG/CPP | Alcohol
2 | 08.12.16 | Dryer Circulation Pump | P-431A | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | RANA | DFA
3 | 11.12.16 | Crude oil transfer pump-1 | P-802A | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | T/F | CPP | TANKFARM
4 | 12.12.16 | Crude oil transfer pump-3 | P-802C | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | CPP | TANKFARM
5 | 17.12.16 | Circulation pump for 01D1 | 01G1A | 55/2900 | 6315 C3/ 6215 C3 | CM | CPP/BHP | Alcohol
6 | 25.12.16 | Boiler feed water pump 3TPH | 07U1G2B | 7.5/ 2900 | 6206 ZZ C3/ 6308 ZZ C3 | Old Boiler | RSG | Old Boiler
2017-01-01
1 | 10.01.17 | Hotwell pump | D-1-1 | 30/2900 | 6311 ZZ C3/ 6311 ZZ C3 | CM | SAL | DFA
2 | 10.01.17 | Air Blower 16-A | 09U1G16A | 55/ 1440 | 6215 C3/ 6215 C3 | ETP | SAL | ETP
3 | 10.01.17 | Intermediate Transfer Pump | 08G20 | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | CM | SAL | T/F GR. FLOOR
4 | 12.01.17 | Trolly Unloading Pump-1 | P-801A | 5.5/ 2900 | 6208 ZZ C3/ 6208 ZZ C3 | CM | SAL | LOOP REACTOR
5 | 16.01.17 | Pestillator Forklift Stering Motor | Stering Motor | 0.65/ 2100 | 6303 ZZ C3/ 6006 2RS | Pestillator | SAL | Pestillator
6 | 14.01.17 | High Pressure Fat Feed Pump | P-201 | 30/1440 | 6213 ZZ C3/ 6212 ZZ C3 | CM | SAL | Splitting
7 | 16.01.17 | HOT WATER PUMP-1 | P-1015A | 18.5/2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | SAL | CPP
8 | 31.01.17 | Collective Water Pump (T/F) | P-832 | 7.5/ 2900 | 6307 ZZ C3/ 6308 ZZ C3 | New T/F | SAL | New T/F
2017-02-01
1 | 02.02.17 | Water ring vacuum pump | VP-27A | 15/2900 | 6309 ZZ C3/ 6309 ZZ C3 | CM | SAL | DFA
2 | 04.02.17 | HOT WATER PUMP-1 | P-1015A | 18.5/2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | SAL | CPP
3 | 04.02.17 | H2 Compressor | 02G1A | 470/495 | 6326 M C3/ 6326 M C3 INSULATED | - | DOL ELECT. | H2 COMP.
4 | 05.02.17 | RO Cartridge feed Pump | 09U1G25 | 5.5/2900 | 6208 ZZ C3/ 6208 ZZ C3 | ETP | SAL | ETP
5 | 05.02.17 | Crude oil transfer pump-3 | P-802C | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | T/F | BHP | TANKFARM
6 | 06.02.17 | F.D.Fan | 10G01C | 160/2900 | 6316 C4/ 6316 C4 | CM | SAL | ALCOHOL
7 | 07.02.17 | BWF pumps | 10G04A | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | SAL | ALCOHOL
8 | 09.02.17 | BWF pumps | 10G04B | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | SAL | ALCOHOL
9 | 16.02.17 | Air Blower | 09U1G17 | 18.5/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | SAL | ETP
10 | 28.02.17 | D-20 DM water V-303 | P-34A | 7.5/2900 | 6207 ZZ C3/ 6208 ZZ C3 | DFA | SAL | DFA
2017-03-01
1 | 05.03.17 | FORCED DRAFT FAN - 1 | P-1052A | 125/1440 | 6319 C3/ 6319 C3 | CHP | SAL | CHP
2 | 06.03.17 | Condensate Transfer Pump | P-8001B | 5.5/2900 | 6208 ZZ C3/ 6208 ZZ C3 | CM | RSM | PRECON
3 | 09.03.17 | ETP Pit Pump | P-913B | 2.2/2900 | 6205 ZZ C3/ 6205 ZZ C3 | - | CPP | OLD BOILER
4 | 12.03.17 | Intermediate FA transfer pump | 08G5B | 30/2900 | 6212 ZZ C2/ 6313 ZZ C3 | - | RSM | TANKFARM
5 | 16.03.17 | CT FAN-1 | P-1016A | 15/1440 | 6309 ZZ C3/ 6309 ZZ C3 | - | RNP | CPP
6 | 22.03.17 | Reboiler circulation pump-1 | P-307A | 15/1440 | 6309 ZZ C3/ 6309 ZZ C3 | - | RNP | DFA
7 | 22.03.17 | Hot oil circulation pump-2 | P-312B | 18.5/1440 | 6310 ZZ C3/ 6310 ZZ C3 | - | SAL | DFA
8 | 23.03.17 | H2 Compressor lubricator | 02G1G3 | 0.25/1400 | 6202 ZZC3/ 6004 ZZ C3 | - | CPP | H2 COMP.
9 | 27.03.17 | BWF pumps | 10G04B | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | CPP/ SAL | ALCOHOL
10 | 29.03.17 | Hot oil dooster pump-2 | P-318B | 5.5/2900 | 6206 ZZ C3/ 6206 ZZ C3 | - | RNP | DFA

## Burnt motor (hidden)
Sr.No. | DATE | Equipment Name | MOTOR TAG | M/C NO. | KW | RPM | Bearing No. | Reported By | SENT TO | Location | Reason
1 | 12.05.14 | DEODERIZER DRYER RECIRCULATION PUMP | P-7102 |  | 2.2 | 2900 |  |  | SANJAY RAJ ELECTRICAL | GDP
2 | 29.05.14 | SAF GD-03 | P-1008 |  | 4 | 2950 | 6306/ZZC3 | SAL | SANJAY RAJ ELECTRICAL | CPP
3 | 16.06.14 | ETP Three Phase submersible pump | [6 empty] | SANJAY RAJ ELECTRICAL | ETP
4 | 10.07.2014 | Utility DM Agitator |  |  | 0.55 | 910 |  | SAL/CPP | SANJAY RAJ ELECTRICAL | Old Boiler
5 | 19.7.2014 |  | P-655 |  | 22 | 1475 | 6310ZZC3 | CPP | SANJAY RAJ ELECTRICAL | CGS
6 | 3.08.2014 | X-FER PUMP FROM HOT WELL TO COOLING WATER | P-7114B |  | 18.5 | 2910 | 6309ZZC3/6308ZZC3 | CPP/SKP | SANJAY RAJ ELECTRICAL | GDP gnd floor
7 | 13.10.14 | Froced draft fan bioler 3TPH | 07U1G1B |  | 11 | 2910 | 6209ZZC3 | CPP/SKP | SANJAY RAJ ELECTRICAL | Utility
8 | 3.11.2014 | CPP CT fan-2 | P-1016B |  | 15 | 1450 | 6309ZZC3 | RSM | SANJAY RAJ ELECTRICAL | CPP
9 | 9.11.2014 | DEODERIZER DRYER RECIRCULATION PUMP | P-7102 | Sr no-72525 | 2.2 | 2840 |  | cpp/skp | SANJAY RAJ ELECTRICAL | GDP
10 | 9.11.2014 | DC hydraulic motor of forklift |  |  | 7.5kw |  |  | cpp | SANJAY RAJ ELECTRICAL | Flaker
11 | 06.12.14 | Agitator for 08T9C | 08N14C |  | 4 | 1440 |  | CPP/SKP | SANJAY RAJ ELECTRICAL | Old tankfarm
12 | 16.12.14 | CPP Seal Air Fan | P-1008 |  | 4 | 2950 | 6306ZZC3 | RSG/DLK | SANJAY RAJ ELECTRICAL | CPP gnd floor
13 | 25.12.14 | Vaccum pump | VP-451B |  | 11 | 1450 | 6309ZZ/6209ZZ | BBL | SANJAY RAJ ELECTRICAL | Jutasama 6th floor
14 | 21.3.15 |  | P-802B |  | 15 | 2930 | 6309ZZC3/6209ZZC3 | BBL | SANJAY RAJ ELECTRICAL | LOOP ground floor
15 | 24.3.15 |  | X-201 |  | 7.5 | 1440 | 6308ZZC3/6208ZZC3 | kirloskar | SANJAY RAJ ELECTRICAL | DFA 5th floor
16 | 26.4.15 |  | P-309B | N2409591 | 9.3 | 2930 | 6208ZZC3 | BBL | SANJAY RAJ ELECTRICAL | DFA gnd floor
17 | 30.5.15 | Agitator for Tank-828 | Tank-828 Agitator | 32391 | 3.7 | 960 | 6308ZZC3/6307ZZC3 | ABB | SANJAY RAJ ELECTRICAL | New TF
18 | 6.5.15 |  | 08N18A |  | 2.2 | 1420 |  |  | SANJAY RAJ ELECTRICAL | Old TF
19 | 26.6.15 |  | P-515B | [5 empty] | SANJAY RAJ ELECTRICAL
20 | 8.7.15 | Mix bed blower motor |  |  | 2.2 | 1425 |  | SAL | SANJAY RAJ ELECTRICAL | Old boiler
21 | 6.9.15 |  | P-168.5 |  | 0.75 | 935 | 6205ZZC3 |  | SANJAY RAJ ELECTRICAL | CGS gnd floor
22 | 23.8.15 |  | P-515B |  | 18.5 | 2920 | 6309ZZC3/6209ZZC3 | cpp
23 | 11.10.15 | Recycle Compressor | 02G3 |  | 330 | 16pole | 6326MC3 | avv | DOL Electric | H2 compressor house
24 | 12.3.16 | Vaccum pump Alfa level Postcon | P-651A |  | 15KW | 4 | 63092RS/6209-2RS | RSG/DLK | SANJAY RAJ ELECTRICAL | Alfa Level Postcon
25 | 11.3.16 | Septic Pump | Septic |  | 1.5KW | NA | NA | RNP/GTC | SANJAY RAJ ELECTRICAL | ETP
26 | 9.3.16 | Pit pump |  |  | 0.55 | 2 | NA | AVV | SANJAY RAJ ELECTRICAL | Pit pump Alcohol
27 | 10.3.16 | E-Wax Agitator | E-Wax |  | NA | NA | NA | RNP/GTC | SANJAY RAJ ELECTRICAL | Patillator
28 | 3.3.16 | Agitator Motor 09U1G21A | 09U1G21A |  | 5.5 | 2 | 6208ZZC3 | RSM/CPP | SANJAY RAJ ELECTRICAL | ETP
29 | 2.4.16 | 06G1G Dryer motor | Dryer Motor |  | 0.55 |  | 6002ZZ | SAL | SANJAY RAJ ELECTRICAL | DFA Air Compressor
30 | 22.4.16 | Safex Motor Hoist | Hoisting motor |  | 1.1 | 1400 | NA | Subhash | SANJAY RAJ ELECTRICAL | Coal Heater
31 | 12.5.16 | Cooling water motor | 20P03B |  | 110 | 1485 | 6319C/6316C3 | RSM | PO work in progress | GDP
32 | 20.5.16 | Hydrogen Compressor Motor | 02G1 |  | 435 | 480 | 6326MC3/6326MC3 | RSM/RSG | DOL Electric | H2 compressor house
33 | 2016-06-16 | NO ANY MOTOR BURNT
34 | 05.07.16 | Cold well pump to steel belt | P-961 |  | 18.5 | 2900 | 6309ZZ/6209ZZ | RNP | SANJAY RAJ ELECTRICAL | Pestillator
35 | 20.08.16 | Decoderizer dryer pump | P-7102 |  | 2.2 | 2900 | - | BHIM | SANJAY RAJ ELECTRICAL | -
36 | 08.09.16 | TANKFARM FEED PUMP | P-7100A |  | 9.3 | 2900 | 6308ZZ/ 6308ZZ | BHIM | SANJAY RAJ ELECTRICAL | GLYCERIEN
37 | 22.10.16 | E-13 Condensate transferring pump | P-31B |  | 7.5 | 2900 | - | CPP | SANJAY RAJ ELECTRICAL | DFA 3RD FLOOR
38 | 27.10.16 | AUX.AIR FAN B | P-1001B |  | 2.2 | 2900 | 6205 ZZ/ 6205 ZZ | CPP/ RSM | SANJAY RAJ ELECTRICAL | CPP
39 | 10.11.16 | TANK FORM FEED PUMP | P-7100A |  | 9.3 | 2900 | 6308ZZ/ 6308ZZ | BHIM | SANJAY RAJ ELECTRICAL | GLYCERIEN | Motor Bearing was jam
40 | 15.11.16 | Air compressor | 06G1A |  | 90 | 1440 | 6317 C3/ 6317 C3 | CPP | DOL Electric | Utility | Winding insulation fail.
41 | 15.11.16 | Spare 110 KW motor |  |  | 110 | 2900 | 6316 C3/ 6319 C3 |  | DOL Electric | Utility | Winding insulation fail.
42 | 24.11.16 | Vaccum Pump | VP-7103B |  | 5.5 | 1440 | - | RSM | SANJAY RAJ ELECTRICAL | GLYCERIEN | Winding resistance unbalance
43 | 19.12.16 | ATFD FEED PUMP | P-7120 |  | 3.7 | 2900 | 6206 ZZ C3/ 6206 ZZ C3 | DLK | SANJAY RAJ ELECTRICAL | GDP | Winding insulation fail.
44 | 16.01.17 | Pestillator Forklift Stering Motor | Stering Motor |  | 0.65 | 2100 | 6303 ZZ C3/ 6006 2RS | AVV | SANJAY RAJ ELECTRICAL | Pestillator | Winding insulation fail.
45 | 03.02.17 | Hot well to Cooling tower pump | 01G19B |  | 18.5 | 2900 | 6209 ZZ C3/6309 ZZ C3 | RSM | SANJAY RAJ ELECTRICAL | ALCOHOL | Motor Bearing was jam
46 | 15.02.17 | CT FAN-2 | P-1016B |  | 15 | 1400 | 6209 ZZ C3/6309 ZZ C3 | RNP/CPP | SANJAY RAJ ELECTRICAL | CPP | Motor bearing housing fully rubbed & rotor touched to stator
47 | 19.02.17 | Degasser Blower | Degasser Blower |  | 0.37 | 2900 | - | CPP | SANJAY RAJ ELECTRICAL | Old Boiler | Winding insulation fail.
48 | 20.02.17 | ETP Three Phase submersible pump | ETP Submerge Pump |  | 2.2 | 2900 | - | DLK | SANJAY RAJ ELECTRICAL | ETP | Winding resistance unbalance
49 | 23.02.17 | Condensate Pump | 07G7B |  | 0.55 | 2900 | - | CPP | SANJAY RAJ ELECTRICAL | ALCOHOL | Moisture inside Motor
50 | 01.03.17 | Feed pump to D-10 | P-3B |  | 3.7 | 2900 | 6206 ZZ C3/ 6206 ZZ C3 | CPP | SANJAY RAJ ELECTRICAL | DFA | Winding insulation fail.
51 | 01.03.17 | RESIDUE TRANSFER PUMP | P-7104A |  | 3.7 | 2900 | 6206 ZZ C3/ 6206 ZZ C3 | DLK | SANJAY RAJ ELECTRICAL | GDP | Winding insulation fail.
52

## SUMMARY
[5 empty] | Count Year wise |  | 32 | 25 | 67 | 37 | 95 | 153 | 97 | 91 | 89 | 68
Sr.No | Description | Tag No. | MCC FeederNo. | Make | HP/KW |  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | Count
1 | Spent lye feed pump | P-150.1 |  |  | 1.5kw | 09.12.13 | [6 empty] | 09.12.13 |  |  |  |  | 1
2 | Old Flakar Drum Motor |  |  | SIEMENS | 15/11 | [12 empty] | 0
3 | wax ester pump | 01G10A | NMCC-2F1 | Bharat Bijiee | 5/3.7 | 11.04.08 |  | 11.04.08 | [9 empty] | 1
4 | wax ester pump | 01G10B | NMCC 2F3 | Bharat Bijiee | 5/3.7 | 21.02.09 |  |  | 21.02.09 | [8 empty] | 1
5 | 01D11 Transfer Pump | 01G11A | EMCC-4F3 | BBL | 75/55 | 15.01.1023.05.1118.06.13 |  |  |  | 15.01.10 | 23.05.11 |  | 18.06.13 |  | 17.07.15 |  |  | 4
6 | 01D11 Transfer Pump | 01G11B | EMCC-4R1 | SIEMENS | 75/55 | 15.01.10 |  |  |  | 15.01.10 | [7 empty] | 1
7 | LIQUID RING VACCCUM PUMP | 01G12 | NMCC-3F1 | ABB | 12.5/9.3 | [12 empty] | 0
8 | LIQUID RING VACCCUM PUMP | 01G12A | M01/BUS-C/31F2 | Kirloskar | 20/15 | 08.01.13 | [6 empty] | 08.01.13 |  |  |  |  | 1
9 | LIQUID RING VACCCUM PUMP | 01G12B | M01/BUS-B/18F2 | SIEMENS | 10/7.5 | 08.01.13 | [6 empty] | 08.01.13 |  | 03.09.2015 |  |  | 2
10 | Reactor Drain out pump | 01G13 | M01/BUS-A/6F1 | BBL | 5/3.7 | [12 empty] | 0
11 | Thermic fluid pump for stripper | 01G13A | NMCC-3F3 | Bharat Bijiee | 20/15 | [12 empty] | 0
12 | Thermic fluid pump for stripper | 01G13B | NMCC-3R3 | Bharat Bijiee | 20/15 | 15.12.09 |  |  | 15.12.09 | [8 empty] | 1
13 | Tempered water pump-III | 01G14A | EMCC-3R2 | BBL | 100/75 | 25.11.0725.05.0823.10.1015.03.11/05.09.1131.12.12 | 25.11.07 | 25.05.08 |  | 23.10.10 | 15.03.11/05.09.11 | 31.12.12 | [5 empty] | 5
14 | Tempered water pump-III | 01G14B | EMCC-2R2 | BBL | 75/55 | 01.12.1101.07.14 spare motor overhauled for upgradation from 55kw to 75 kw. |  |  |  |  | 01.12.11 |  |  | 01.07.14 spare motor overhauled for upgradation from 55kw to 75 kw. |  |  |  | 2
15 | 01D10 Circulation Pump | 01G15A | NMCC-2R2 | BBL | 25/18.5 | [12 empty] | 0
16 | 01D10 Circulation Pump | 01G15B | NMCC4R2 | BBL | 25/18.5 | 30.09.1106.01.13 |  |  |  |  | 30.09.11 |  | 06.01.13 |  |  |  |  | 2
17 | Terpered cooling water III pump | 01G16A | EMCC-4R2 | BBL | 75/55 | 07.09.0707.10.14 | 07.09.07 | [6 empty] | 07.10.14 |  |  |  | 2
18 | Terpered cooling water III pump | 01G16B | EMCC-3R1 | BBL | 75/55 | 18.09.0720.11.12 | 18.09.07 |  |  |  |  | 20.11.12 | [5 empty] | 2
19 | Scrubber Pump( FAP 3rd Floor) | 01G17A | M01/HYMCC-2F1 | BBL | 1.5/2 | 10.12.13 | [6 empty] | 10.12.13 |  | 02.12.2015 |  |  | 2
20 | Scrubber Pump( FAP 3rd Floor) | 01G17B | M01/HYMCC-4R3 | BBL | 1.5/2 | [12 empty] | 0
21 | Hot well to Cooling tower pump | 01G19A | PMCC-37R1 | Bharat Bijiee | 20/15 | [12 empty] | 0
22 | Hot well to Cooling tower pump | 01G19B | [12 empty] | 20.11.2015 |  | 03.02.17 | 2
23 | Circulation pump for 01D1 | 01G1A | EMCC/1R1 | ABB | 75/55 | 02.03.13 | [6 empty] | 02.03.13 |  | 01.10.2015 | 17.12.16 |  | 3
24 | Circulation pump for 01D1 | 01G1B | EMCC/1R2 | ABB | 75/55 | [12 empty] | 0
25 | Circulation pump for 01D2 | 01G2A | BUS-C-EXT/37F2 | ABB | 30/22 | 05.06.14 | [7 empty] | 05.06.14 |  |  |  | 1
26 | Circulation pump for 01D2 | 01G2B | BUS-C-EXT/37F3 | BBL | 40/30 | 17.12.09 |  |  | 17.12.09 | [8 empty] | 1
27 | Circulation pump for 01D3 | 01G3A | EMCC-3F1 | BBL | 40/30 | 16.08.14 | [7 empty] | 16.08.14 |  |  |  | 1
28 | Circulation pump for 01D3 | 01G3B | EMCC-4F1 | ABB | 30/22 | [12 empty] | 0
29 | Circulation pump for 01D4 | 01G4A | EMCC-1F3 | ABB | 75/55 | 10.06.14 | [7 empty] | 10.06.14 |  |  |  | 1
30 | Circulation pump for 01D4 | 01G4B | EMCC-3F3 | ABB | 75/55 | 05.07.10 |  |  |  | 05.07.10 | [7 empty] | 1
31 | Inline pump for 01E1 | 01G5A | NMCC-2F4 | ABB | 10/7.5 | 11.09.14 | [7 empty] | 11.09.14 |  |  |  | 1
32 | Inline pump for 01E1 | 01G5B | NMCC-2R3 | ABB | 10/7.5 | [9 empty] | 5.09.2015 | 17.08.16 |  | 2
33 | Inline pump for 01E2 | 01G6A | M01/BUS-A/7F5 | ABB | 10/7.5 | 30.11.1004.08.11 |  |  |  | 30.11.10 | 04.08.11 |  |  |  | 22.07.15 |  |  | 3
34 | Inline pump for 01E2 | 01G6B | M01/BUS-A/7F6 | ABB | 10/7.5 | 08.09.13 | [6 empty] | 08.09.13 |  |  |  |  | 1
35 | Inline pump for 01E3 | 01G7A | M01/BUS-A/9R1 | ABB | 10/7.5 | 06.04.08 |  | 06.04.08 | [9 empty] | 1
36 | Inline pump for 01E3 | 01G7B | M01/BUS-A/9R2 | ABB | 10/7.5 | [12 empty] | 0
37 | Inline pump for 01E4 | 01G8A | M01/BUS-A/9R3 | ABB | 10/7.5 | [12 empty] | 0
38 | Inline pump for 01E4 | 01G8B | M01/BUS-A/11R1 | ABB | 10/7.5 | 06.04.0811.07.12 |  | 06.04.08 |  |  |  | 11.07.12 | [5 empty] | 2
39 | Inline pump for 01E8 | 01G9A | M01/NMCC-3F4 | ABB | 10/7.5 | [12 empty] | 0
40 | Inline pump for 01E8 | 01G9A | EMCC-3F4 |  | 37 | [12 empty] | 0
41 | Inline pump for 01E8 | 01G9B | M01/NMCC-4F4 | ABB | 10/7.5 | [12 empty] | 0
42 | Inline pump for 01E8 | 01G9B | EMCC-4F3 |  | 37 | [12 empty] | 0
43 | H2 Compressor | 02G1 | M01/BUS-A/2F1 | LOHER | 580/435 | 30.05.0902.03.10 |  |  | 30.05.09 | 02.03.10 |  |  |  |  | 13.04.15 | 20.05.2016 |  | 4
44 | H2 Compressor | 02G1A | NPMCC/ 8F1 | LOHER | 470 | [11 empty] | 04.02.17 | 1
45 | H2 Compressor main lub oil pump | 02G1AG1 | NPMCC/3F6 | ABB | 3/2.2 | 24.10.0921.12.13 |  |  | 24.10.09 |  |  |  | 21.12.13 |  |  |  |  | 2
46 | H2 Compressor Aux.lub oil pump | 02G1AG2 | NPMCC /16F1 | BHARAT BIJALI | 3/2.2 | 24.10.09 |  |  | 24.10.09 | [8 empty] | 1
47 | H2 Compressor lubricator | 02G1AG3 | NPMCC /3F1 | LOHER | 0.55 | [12 empty] | 0
48 | H2 Compressor main lub oil pump | 02G1G1 | M01/BUS-A/11F2 | Crompton Greaves | 2/1.5 | 27.02.10 |  |  |  | 27.02.10 | [7 empty] | 1
49 | H2 Compressor Aux.lub oil pump | 02G1G2 | M01/BUS-A/11F3 | Crompton Greaves | 2/1.5 | 17.05.0903.03.10 |  |  | 17.05.09 | 03.03.10 | [7 empty] | 2
50 | H2 Compressor lubricator | 02G1G3 | M01/BUS-A/11F4 | Felten & Guilleaume | .32/.25 | 04.03.10 |  |  |  | 04.03.10 | [6 empty] | 23.03.17 | 2
51 | Recycle Compressor | 02G3 | M01/BUS-C/27F1 | LOHER | 440/330 | [9 empty] | 25.06.15/26.08.2015/ 11.10.2015 |  |  | 1
52 | Recycle Comp. main lub oil pump | 02G3G1 | M01/BUS-C/33F1 | Crompton Greaves | 1.5/1.1 | [9 empty] | 31.08.2015 |  |  | 1
53 | Recycle Comp. Aux. lub oil pump | 02G3G2 | M01/BUS-C/33F2 | Crompton Greaves | 1.5/1.1 | 17.05.09 |  |  | 17.05.09 | [8 empty] | 1
54 | Recycle Compressor lubricator | 02G3G3 | M01/BUS-C/36F1 | Felten & Guilleaume | .32/.25 | [12 empty] | 0
55 | HP wax ester feed pump | 02G5A | M01/VFD1 | LOHER | 320/250 | 01.08.12 | [5 empty] | 01.08.12 | [5 empty] | 1
56 | HP wax sealing pump motor | 02G5AG1 | M01/BUS-C/36F2 | Cemp Milano | 1/.75 | [9 empty] | 28.02.15 |  |  | 1
57 | HP wax ester feed pump | 02G5B | M01/VFD2 | LOHER | 320/250 | 02.08.12 | [5 empty] | 02.08.12 | [5 empty] | 1
58 | HP wax sealing pump motor | 02G5BG1 | M01/BUS-C/36F3 | Cemp Milano | 1/.75 | [12 empty] | 0
59 | HP wax ester feed pump | 02G5C | M01/VFD3 | LOHER | 320/250 | 10.12.12 | [5 empty] | 10.12.12 | [5 empty] | 1
60 | HP wax sealing pump motor | 02G5CG1 | M01/BUS-C/36F4 | Cemp Milano | 1/.75 | [12 empty] | 0
61 | Booster Pump | 02G7 C | MO1/BUS-A/6F4 | ABB | 15/11 | [12 empty] | 0
62 | Crude alcohol pump | 02G7A | EMCC/2F1 | BBL | 40/30 | 06.09.12 | [5 empty] | 06.09.12 | [5 empty] | 1
63 | Crude alcohol pump | 02G7B | MO1/BUS-C/34R1 | ABB | 25/18.5 | 28.09.11 |  |  |  |  | 28.09.11 | [6 empty] | 1
64 | Section-3 feed pump-1 | 02G8A | NPMCC-4R2 | BBL | 37 | [9 empty] | 07.02.15 |  |  | 1
65 | Section-3 feed pump-1 | 02G8B | NPMCC-13R2 | BBL | 37 | [12 empty] | 0
66 | Residue recycle pump | 03G14A | M01/BUS-A/8F1 | ABB | 7.5/5.5 | [12 empty] | 0
67 | Residue recycle pump | 03G14B | M01/BUS-A/8F2 | ABB | 7.5/5.5 | 25.03.11 |  |  |  |  | 25.03.11 | [6 empty] | 1
68 | Circulation pump | 03G15A | M01/BUS-A/5F3 | ABB | 25/18.5 | 24.05.12 | [5 empty] | 24.05.12 | [5 empty] | 1
69 | Circulation pump | 03G15B | M01/BUS-A/4F3 | ABB | 25/18.5 | 30.07.10 |  |  |  | 30.07.10 | [5 empty] | 25.11.16 |  | 2
70 | WR Vaccum pump | 03G16G3 | M01/BUS-A/6F3 | Crompton Greaves | 15/11 | 18.05.09 |  |  | 18.05.09 | [8 empty] | 1
71 | Hot Well Pump | 03G17A | M01/BUS-C/36R1 | BBL | 20/15 | [10 empty] | 01.05.16 |  | 1
72 | Hot Well Pump | 03G17B | M01/BUS-C/36R2 | BBL | 20/16 | [9 empty] | 02.10.2015 |  |  | 1
73 | Circulation pump drive cycle | 03G1A | NPMCC-4R1 | BBL | 55 | 11.02.12 | [5 empty] | 11.02.12 | [5 empty] | 1
74 | Circulation pump drive cycle | 03G1B | NPMCC-15F1 | BBL | 55 | [9 empty] | 25.02.15 | 29.02.16 |  | 2
75 | Pump for Distillate | 03G2A | M01/BUS-A/10R4 | ABB | 50/37 | [12 empty] | 0
76 | Pump for Distillate | 03G2B | M01/BUS-A/11R4 | ABB | 50/37 | [12 empty] | 0
77 | Pump for column 03D2 | 03G3A | M01/BUS-A/7R4 | ABB | 50/37 | 10.01.12 | [5 empty] | 10.01.12 |  |  | 26.03.15 | 25.02.2016 |  | 3
78 | Pump for column 03D2 | 03G3B | M01/BUS-A/9R4 | ABB | 50/37 | 05.02.11 |  |  |  |  | 05.02.11 | [6 empty] | 1
79 | Inline pump for thermal oil | 03G4A | M01/BUS-A/9F5 | ABB | 15/11 | 23.10.14 | [7 empty] | 23.10.14 |  |  |  | 1
80 | Inline pump for thermal oil | 03G4B | M01/BUS-A/9F6 | ABB | 15/11 | 19.04.08 |  | 19.04.08 | [9 empty] | 1
81 | Pump for fraction from 03D2 | 03G5A | M01/BUS-A/11F5 | ABB | 7.5/5.5 | 21.10.09 |  |  | 21.10.09 | [8 empty] | 1
82 | Pump for fraction from 03D2 | 03G5B | M01/BUS-A/11F6 | ABB | 7.5/5.5 | 09.09.07 | 09.09.07 | [10 empty] | 1
83 | Pump for fraction from 03D2 | 03G5C | M01/BUS-A/11R3 | ABB | 7.5 | [12 empty] | 0
84 | Inline pump for thermal oil | 03G6A | M01/BUS-A/6R2 | ABB | 15/11 | 18.03.11 |  |  |  |  | 18.03.11 | [6 empty] | 1
85 | Inline pump for thermal oil | 03G6B | M01/BUS-A/6R3 | ABB | 15/11 | 20.11.0720.04.0818.07.09 | 20.11.07 | 20.04.08 | 18.07.09 | [8 empty] | 3
86 | Pump for final Residue | 03G7A | M01/BUS-A/10F1 | ABB | 3/2.2 | [12 empty] | 0
87 | Pump for final Residue | 03G7B | M01/BUS-A/10F2 | ABB | 3/2.2 | [12 empty] | 0
88 | Inline pump for thermal oil | 03G8A | M01/BUS-A/9F1 | ABB | 1.5/1.1 | [12 empty] | 0
89 | Inline pump for thermal oil | 03G8B | M01/BUS-A/9F2 | ABB | 1.5/1.1 | [12 empty] | 0
90 | Inline pump for thermal oil | 03G9A | M01/BUS-A/7F1 | ABB | 10/7.5 | [12 empty] | 0
91 | Inline pump for thermal oil | 03G9B | M01/BUS-A/7F2 | ABB | 10/7.5 | [12 empty] | 0
92 | Product pump | 04G5A | M01/BUS-A/10R1 | ABB | 10/7.5 | 31.08.07 | 31.08.07 | [10 empty] | 1
93 | Product pump | 04G5B | M01/BUS-A/10R2 | ABB | 10/7.5 | 31.08.0714.11.11 | 31.08.07 |  |  |  | 14.11.11 | [6 empty] | 2
94 | Terpered cooling water I pump | 05G10A | M01/BUS-C/30R3 | ABB | 125/90 | 19.01.1020.01.11 |  |  |  | 19.01.10 | 20.01.11 | [6 empty] | 2
95 | Terpered cooling water I pump | 05G10B | M01/BUS-C/32R3 | ABB | 125/90 | [10 empty] | 16.11.16 |  | 1
96 | Terpered cooling water II pump | 05G11A | NPMCC-18F1 | BBL | 15/11 | 28.12.0712.03.1108.09.13 | 28.12.07 |  |  |  | 12.03.11 |  | 08.09.13 |  |  |  |  | 3
97 | Terpered cooling water II pump | 05G11B | NPMCC-18F2 | BBL | 15/11 | 03.10.0703.02.1205.12.13 | 03.10.07 |  |  |  |  | 03.02.12 | 05.12.13 |  | 29.05.15 |  |  | 4
98 | Hot water pump-1 | 05G12A | NPMCC-12R1 | BBL | 45 | [12 empty] | 0
99 | Hot water pump-1 | 05G12B | NPMCC-3R1 | BBL | 45 | [12 empty] | 0
100 | New DM water pump-1 | 05G18A | UMCC/4F4 | BBL | 22 | [12 empty] | 0
101 | New DM water pump-1 | 05G18B | UMCC/4F5 | BBL | 22 | [12 empty] | 0
102 | Raw water pump | 05G1A | UMCC/BUS-A/3R5 | SIEMENS | 25/18.5 | [12 empty] | 0
103 | Raw water pump | 05G1B | UMCC/BUS-B/10R3 | SIEMENS | 25/18.5 | [12 empty] | 0
104 | DM water pump | 05G3A | UMCC/BUS-B/12R1 | SIEMENS | 5.5/4 | 02.02.0921.05.1021.12.1220.05.13 |  |  | 02.02.09 | 21.05.10 |  | 21.12.12 | 20.05.13 |  |  |  |  | 4
105 | DM water pump | 05G3B | UMCC/BUS-B/9F5 | SIEMENS | 5.5/4 | 28.04.14 | [7 empty] | 28.04.14 |  |  |  | 1
106 | DM water pump | 05G3C |  |  |  | 05.12.13 | [6 empty] | 05.12.13 |  |  | 22.05.2016 |  | 2
107 | Drinking water pump | 05G5A | UMCC/BUS-B/11F2 | SIEMENS | 7.5/5.5 | 17.08.13 | [6 empty] | 17.08.13 |  |  |  |  | 1
108 | Drinking water pump | 05G5B | UMCC/BUS-B/11F3 | SIEMENS | 7.5/5.5 | 19.10.0802.10.1017.08.13 |  | 19.10.08 |  | 02.10.10 |  |  | 17.08.13 |  |  |  |  | 3
109 | Fire water pump | 05G7A | UMCC/BUS-B/8F1 | SIEMENS | 175/132 | [12 empty] | 0
110 | Jockey pump | 05G8 | UMCC/BUS-A/2F3 | SIEMENS | 20/15 | 02.11.08 |  | 02.11.08 | [9 empty] | 1
111 | JOCKY PUMP | 05G8A |  |  | 5.5kw | 2.11.08 |  | 2.11.08 | [9 empty] | 1
112 | Cooling water pump | 05G9 F | UMCC/BUS-A/1R5 | Kirloskar | 40/30 | [10 empty] | 25.03.16 |  | 1
113 | Cooling water pump | 05G9A | UMCC/BUS-A/4F1 | SIEMENS | 210/160 | 05.11.11 |  |  |  |  | 05.11.11 | [6 empty] | 1
114 | Cooling water pump | 05G9B | UMCC/BUS-A/3R1 | SIEMENS | 210/160 | [12 empty] | 0
115 | Cooling water pump | 05G9C | UMCC/BUS-A/8R1 | SIEMENS | 210/160 | 30.12.09 |  |  | 30.12.09 | [8 empty] | 1
116 | Cooling water pump | 05G9D | M01/BUS-C/35F4/VFD | Kirloskar | 40/30 | 09.01.09 |  |  | 09.01.09 | [8 empty] | 1
117 | Cooling water pump | 05G9E | M01/BUS-C/35F4/VFD | Kirloskar | 40/30 | 08.01.0914.12.12 |  |  | 08.01.09 |  |  | 14.12.12 |  |  | 28.02.15 |  |  | 3
118 | Cooling water pump | 05G9G | UMCC/BUS-A/3R1 | Kirloskar | 40/30 | 17.02.11 |  |  |  |  | 17.02.11 |  |  |  |  | 16.01.16 |  | 2
119 | Degaser blower | 05U1G1 | UMCC/BUS-B/11F4 | SIEMENS | .5/.37 | 30.07.0825.03.0923.06.13 |  | 30.07.08 | 25.03.09 |  |  |  | 23.06.13 |  |  | 28.08.16 |  | 4
120 | Mixed bed blower | 05U1G2 | UMCC/BUS-B/11R2 | SIEMENS | 3/2.2 | [12 empty] | 0
121 | Deassor water pump | 05U1G3 | UMCC/BUS-B/10R1 | SIEMENS | 5.2/4 | [12 empty] | 0
122 | Agitator for 05U1T2A | 05U1G7A | M01/BUS-A/1F3 | SIEMENS | .5/.37 | 06.06.10 |  |  |  | 06.06.10 | [7 empty] | 1
123 | Agitator for 05U1T2B | 05U1G7B | M01/BUS-A/1F4 | SIEMENS | .5/.37 | [12 empty] | 0
124 | Effluent transfer pump | 05U1G8 | UMCC/BUS-B/13F3 | SIEMENS | 3/2.2 | 25.07.14 | [7 empty] | 25.07.14 |  |  |  | 1
125 | C.T.Unit with fans | 05U2G1A | UMCC/BUS-B/12R2 | SIEMENS | 30/22 | [12 empty] | 0
126 | C.T.Unit with fans | 05U2G1B | UMCC/BUS-B/9R2 | SIEMENS | 30/22 | [12 empty] | 0
127 | Blower for side stream filter | 05U5G1 | UMCC/BUS-A/2F4 | SIEMENS | 3/2.2 | 13.10.10 |  |  |  | 13.10.10 | [7 empty] | 1
128 | Air compressor | 06G1A | M01/BUS-B/22R4 | SIEMENS | 125/90 | [9 empty] | 10.10.2015 |  |  | 1
129 | Air compressor | 06G1B | M01/BUS-B/34R3 | SIEMENS | 125/90 | [12 empty] | 0
130 | Air compressor | 06G1C | M01/BUS-B/36R3 | SIEMENS | 125/90 | [12 empty] | 0
131 | Atlas copco comp-D | 06G1D |  |  | 75kw | 01.11.1112.06.14 |  |  |  |  | 01.11.11 |  |  | 12.06.14 |  | 22.04.16 |  | 3
132 | Atlas copco comp-E | 06G1E |  |  | 55kw | 15.09.10 |  |  |  | 15.09.10 | [7 empty] | 1
133 | Atlas copco comp-G | 06G1G |  |  | 55kw | 27.07.1105.11.14/24.11.14 |  |  |  |  | 27.07.11 |  |  | 05.11.14/24.11.14 | 16.02.15 | 02.04.2016 |  | 4
134 | N2 Booster compressor | 06G2 | M01/Bus-C/31F1 | SIEMENS | 20/15 | [12 empty] | 0
135 | L.P.condensate pump | 07G1A | M01/BUS-C/32F1 | ABB | 2/1.5 | 27.05.1012.02.11 |  |  |  | 27.05.10 | 12.02.11 | [6 empty] | 2
136 | L.P.condensate pump | 07G1B | M01/BUS-C/32F2 | ABB | 2/1.5 | 12.06.1029.10.12 |  |  |  | 12.06.10 |  | 29.10.12 |  |  |  | 01.12.16 |  | 3
137 | FO/LSHS Unloading pump | 07G2A | UMCC/BUS-A/3F1 | Crompton Greaves | 7.5/5.5 | [12 empty] | 0
138 | LDO transfer pump | 07G3A | UMCC/BUS-B/10F5 | Crompton Greaves | 2/1.5 | [12 empty] | 0
139 | LDO transfer pump | 07G3B | UMCC/BUS-B/10F6 | Crompton Greaves | 2/1.5 | [12 empty] | 0
140 | LDO transfer pump | 07G4A | UMCC/BUS-A/2F1 | Crompton Greaves | 5/3.7 | [12 empty] | 0
141 | FO/LSHS Unloading pump | 07G5A | UMCC/BUS-B/11R1 | Crompton Greaves | 2/1.5 | 15.04.2006 | 15.04.2006 | [10 empty] | 1
142 | FO/LSHS Unloading pump | 07G5B | UMCC-BUS-B/13F4 | Crompton Greaves | 2/1.5 | [12 empty] | 0
143 | CONDENSATE PUMP | 07G7A | PMCC-7R2 | [14 empty] | 0
144 | CONDENSATE PUMP | 07G7B | PMCC-11R2 |  |  | 06.12.2014 | [7 empty] | 06.12.2014 |  |  |  | 1
145 | CONDENSATE PUMP | 07G8A | PMCC-7F3 | [14 empty] | 0
146 | CONDENSATE PUMP | 07G8B | PMCC-7F4 | [14 empty] | 0
147 | Froced draft fan bioler 5TPH | 07U1G1A | UMCC/BUS-B/13F4 | SIEMENS | 25/18.5 | 08.11.10/19.10.10/05.02.10 |  |  |  | 08.11.10/19.10.10/05.02.10 |  |  |  |  | 16.02.15/24.06.15 |  |  | 2
148 | Froced draft fan bioler 3TPH | 07U1G1B | UMCC/BUSB/9F2 | SIEMENS | 15/11 | 06.02.0911.05.1309.10.14/13.10.14 |  |  | 06.02.09 |  |  |  | 11.05.13 | 09.10.14/13.10.14 |  |  |  | 3
149 | Bioler feed water pump 3TPH | 07U1G2A | UMCC/BUSB/12F2 | GRUNDFOS | 10/7.5 | 09.10.14 | [7 empty] | 09.10.14 |  |  |  | 1
150 | Bioler feed water pump 3TPH | 07U1G2B | UMCC/BUSB/12F3 | GRUNDFOS | 10/7.5 | 13.07.14/09.10.14 | [7 empty] | 13.07.14/09.10.14 |  | 25.12.16 |  | 2
151 | Bioler feed water pump 5TPH | 07U1G3A | UMCC/BUSB/12F5 | GRUNDFOS | 10/7.5 | 15.11.14 | [7 empty] | 15.11.14 |  |  |  | 1
152 | Bioler feed water pump 5TPH | 07U1G3B | UMCC/BUSB/12F6 | GRUNDFOS | 10/7.5 | 13.11.14 | [7 empty] | 13.11.14 |  |  |  | 1
153 | Fuel oil pump 5TPH | 07U1G5A | UMCC/BUS-B/13F2 | SIEMENS | 3/2.2 | [12 empty] | 0
154 | Fuel oil pump 5TPH | 07U1G5A | UMCC/BUSB/10F3 | SIEMENS | 1.5/1.1 | [12 empty] | 0
155 | Fuel oil pump 5TPH | 07U1G5B | UMCC/BUSB/9F3 | SIEMENS | 3/2.2 | [12 empty] | 0
156 | Fuel oil pump 5TPH | 07U1G5B | UMCC/BUSB/10F4 | SIEMENS | 1.5/1.1 | [12 empty] | 0
157 | Ring main pump | 07U1G7A | UMCC/BUSB/10F1 | SIEMENS | 1.5/1.1 | [12 empty] | 0
158 | Ring main pump | 07U1G7B | UMCC/BUSB/10F2 | SIEMENS | 1.5/1.1 | [12 empty] | 0
159 | Agitator for doasing | 07U1G8 | UMCC/BUSB/1F5 | SIEMENS | .5/.37 | [12 empty] | 0
160 | Bolier Process Water pump | 07U1G9A |  |  | 2.2kw | 12.04.08 |  | 12.04.08 | [9 empty] | 1
161 | boiler pump | 07U1G9B |  |  |  | 01.09.08 |  | 01.09.08 | [9 empty] | 1
162 | Electrical Heater | 07U2E4A | M01/BUS-B/22F6 | [14 empty] | 0
163 | Electrical Heater | 07U2E4B | M01/BUS-A/18F6 | [14 empty] | 0
164 | Thermic fluid pump | 07U2G1A | M01/BUS-C/29F1 | ABB | 150/110 | [9 empty] | 11.04.15 |  |  | 1
165 | Thermic fluid pump | 07U2G1B | M01/BUS-C/28F1 | ABB | 150/110 | 24.12.11 |  |  |  |  | 24.12.11 |  |  |  | 07.02.15 |  |  | 2
166 | Forced draft fan | 07U2G2A | M01/BUS-C/29R4 | ABB | 50/37 | 31.08.0723.12.11 | 31.08.07 |  |  |  | 23.12.11 | [6 empty] | 2
167 | Forced draft fan | 07U2G2B | M01/BUS-C/33R3 | ABB | 50/37 | 18.08.1023.10.1130.09.13 |  |  |  | 18.08.10 | 23.10.11 |  | 30.09.13 |  |  |  |  | 3
168 | Sump pump | 07U2G5 | M01/BUS-B/20F3 | ABB | 7.5/5.5 | [12 empty] | 0
169 | Ring main pump | 07U2G6A | M01/BUS-C/35F1 | ABB | 3/2.5 | [12 empty] | 0
170 | Ring main pump | 07U2G6B | M01/BUS-C/35F2 | ABB | 3/2.5 | 28.09.0717.10.13 | 28.09.07 | [5 empty] | 17.10.13 |  |  |  |  | 2
171 | LSHS/FO fuel pump | 07U2G7A | M01/BUS-C/36F6 | ABB | 3/2.2 | [12 empty] | 0
172 | LSHS/FO fuel pump | 07U2G7B | M01/BUS-C/34F1 | ABB | 3/2.2 | [12 empty] | 0
173 | LSHS/FO fuel pump | 07U2G7C | M01/BUS-C/34F2 | ABB | 3/2.2 | [12 empty] | 0
174 | LSHS/FO fuel pump | 07U2G7D | M01/BUS-C/34F3 | ABB | 3/2.2 | [12 empty] | 0
175 | LDO fuel pump | 07U2G8A | M01/BUS-C/34F4 | ABB | 3/2.2 | [12 empty] | 0
176 | LDO fuel pump | 07U2G8B | M01/BUS-C/34F5 | ABB | 3/2.2 | [12 empty] | 0
177 | Circulation pump | 07U3G1C | NPMCC112/15R1 | BBL | 100/75 | [12 empty] | 0
178 | Circulation pump | 07U3G1D | NPMCC112/6R1 | BBL | 100/75 | 20.11.13 | [6 empty] | 20.11.13 |  |  |  |  | 1
179 | Thermic Heater Pump | 07U3G1E | UMCC/4R4 |  | 75 | [12 empty] | 0
180 | Thermic Heater Pump | 07U3G1F | UMCC/5R1 |  | 75 | [12 empty] | 0
181 | FD fan | 07U3G2C | NPMCC112/7F1 | BBL | 40/30 | [12 empty] | 0
182 | Furnace oil pump | 07U3G3C | NPMCC112/12F1 | BBL | 3/2.2 | [12 empty] | 0
183 | Furnace oil pump | 07U3G3D | NPMCC112/3F3 | BBL | 3/2.2 | [12 empty] | 0
184 | ring main pump | 07U3G4C | NPMCC112/3F4 | BBL | 3/2.2 | [12 empty] | 0
185 | ring main pump | 07U3G4D | NPMCC112/12F2 | BBL | 3/2.2 | [12 empty] | 0
186 | LDO pump | 07U3G6C | NPMCC112/3F5 | BBL | 3/2.2 | [12 empty] | 0
187 | Naptha transfer pump vertical | 08G10A | M01/BUS-A/6F2 | Crompton Greaves | 7.5/5.5 | 26.07.0927.01.11 |  |  | 26.07.09 |  | 27.01.11 | [6 empty] | 2
188 | NAPTH TRANSFER PUMP | 08G10B | PMMC-7R1 |  |  | 03.12.0726.07.09 | 03.12.07 |  | 26.07.09 | [8 empty] | 2
189 | Nafth unloading pump | 08G13A | M01/BUS-A/11F1 | Crompton Greaves | 2/1.5 | [12 empty] | 0
190 | Agitator for 08T9D | 08G14D | M01/BUS-B/18F3 | SIEMENS | 5.5/4 | [12 empty] | 0
191 | Fatty acid unloading pump | 08G1A | M01/BUS-B/22R1 | SIEMENS | 20/15 | [12 empty] | 0
192 | Fatty acid unloading pump | 08G1B | M01/BUS-B/22R2 | SIEMENS | 20/15 | [12 empty] | 0
193 | Fatty acid unloading pump | 08G1C | M01/BUS-B/22R3 | SIEMENS | 20/15 | [12 empty] | 0
194 | Intermediate Transfer Pump | 08G20 | PAST-5F3 | SIEMENS | 22 | [11 empty] | 10.01.17 | 1
195 | Intermediate Transfer Pump | 08G21 | PAST-5F2 | Bharat Bijiee | 22 | [12 empty] | 0
196 | Intermediate Transfer Pump | 08G22 | 2F1 | Bharat Bijiee | 22 | [12 empty] | 0
197 | Intermediate Transfer Pump | 08G23 | 5F4 | SIEMENS | 18.5 | [12 empty] | 0
198 | Intermediate Transfer Pump | 08G24 | PAST-4F1 | Bharat Bijiee | 22 | [12 empty] | 0
199 | Intermediate Transfer Pump | 08G25 | 5F1 | SIEMENS | 18.5 | [12 empty] | 0
200 | Fatty acid transfer pump | 08G2A | M01/BUS-B/17F2 | SIEMENS | 12.5/9.3 | 10.04.11 |  |  |  |  | 10.04.11 | [6 empty] | 1
201 | Fatty acid transfer pump | 08G2B | M01/BUS-B/18R3 | SIEMENS | 12.5/9.3 | [12 empty] | 0
202 | Fatty Alcohol product filling pump | 08G3A | M01/BUS-B/17R1 | ABB | 30/22 | 11.04.1118.07.12 |  |  |  |  | 11.04.11 | 18.07.12 | [5 empty] | 2
203 |  | 08G5B | N.PMCC/ 7F2 | BBL | 30 | [11 empty] | 12.03.17 | 1
203 | Naptha transfer pump | 08G8B | M01/BUS-B/22F2 | Crompton Greaves | 3/2.2 | 14.10.07 | 14.10.07 | [10 empty] | 1
204 | Agitator for 08T9C | 08N14C | M01/BUS-B/21F3 | SIEMENS | 5.5/4 | 08.12.14 | [7 empty] | 08.12.14 |  |  |  | 1
205 | Agitator for 08T005 | 08N16A | M01/BUS-B/20F6 | SIEMENS | 2/1.5 | [9 empty] | 11.05.15 |  |  | 1
206 | Agitator for 08TGB | 08N17B | M01/BUS-B/20F2 | SIEMENS | 3/2.2 | [12 empty] | 0
207 | Agitator for 08TGC | 08N17C | M01/BUS-B/20F3 | SIEMENS | 3/2.2 | [12 empty] | 0
208 | Agitator for 08TGD | 08N17D | M01/BUS-B/20F4 | SIEMENS | 3/2.2 | [12 empty] | 0
209 | Agitator for 08T4E | 08N17E | M01/BUS-B/20F5 | SIEMENS | 3/2.2 | [12 empty] | 0
210 | Agitator for 08T3A | 08N18A | M01/BUS-B/17F3 | SIEMENS | 3/2.2 | 11.04.13 | [6 empty] | 11.04.13 |  | 06.05.2015 |  |  | 2
211 | Agitator for 08T3B | 08N18B | M01/BUS-B/19R1 | SIEMENS | 3/2.2 | 15.04.0731.12.14 | 15.04.07 | [6 empty] | 31.12.14 |  |  |  | 2
212 | Soap pump for process | 09G2 | M01/BUS-A/9F3 | SIEMENS | 5.5/4 | 24.06.10 |  |  |  | 24.06.10 | [7 empty] | 1
213 | Soap pump for process | 09G3 | M01/BUS-B/19F2 | SIEMENS | [13 empty] | 0
214 | Effluent transfer pump | 09G4 A | M01/BUS-B/22F3 | Crompton Greaves | 5/3.7 | 17.02.09 |  |  | 17.02.09 | [8 empty] | 1
215 | Effluent transfer pump | 09G4 B | M01/BUS-A/7R3 | Crompton Greaves | 5/3.7 | [12 empty] | 0
216 | Effluent transfer pump | 09G5 | M01/BUS-B/22F4 | Kirloskar | 3/2.2 | [12 empty] | 0
217 | Centrifuge | 09U1D14 | ETPMCC/9R5 | Bharat Bijiee | 20/15 | [12 empty] | 0
218 | pH Correction Tank Agitator | 09U1G10 | ETPMCC/5R4 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
219 | HRSCC Feed Pump A | 09U1G11A | ETPMCC/6R1 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
220 | HRSCC Feed Pump B | 09U1G11B | ETPMCC/6R4 | ABB | 1.5/1.1 | [12 empty] | 0
221 | pHCT Agitator | 09U1G12 | ETPMCC/6R5 | Bharat Bijiee | 1.5/1.1 | 03.01.10 |  |  |  | 03.01.10 | [7 empty] | 1
222 | Centrifuge feed pump- A | 09U1G13A | ETPMCC/7R3 | Bharat Bijiee | 1.5/1.1 | 24.08.08 |  | 24.08.08 | [9 empty] | 1
223 | Centrifuge feed pump- B | 09U1G13B | ETPMCC/7R2 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
224 | Bio Tower Feed Pump A | 09U1G14A | ETPMCC/8R1 | Bharat Bijiee | 3/2.2 | [12 empty] | 0
225 | Bio Tower Feed Pump B | 09U1G14B | ETPMCC/8R2 | Bharat Bijiee | 3/2.2 | [12 empty] | 0
226 | Bio Tower Recirculation - A | 09U1G15A | ETPMCC/2F3 | Bharat Bijiee | 5/3.7 | 07.06.0919.07.12/20.08.12 |  |  | 07.06.09 |  |  | 19.07.12/20.08.12 | [5 empty] | 2
227 | Bio Tower Recirculation - B | 09U1G15B | ETPMCC/2F4 | Bharat Bijiee | 5/3.7 | 18.09.13 | [6 empty] | 18.09.13 |  | 29.06.15 |  |  | 2
228 | Air Blower 16-A | 09U1G16A | ETPMCC/1F3 | Bharat Bijiee | 75/55 | 30.07.0803.06.13 |  | 30.07.08 |  |  |  |  | 03.06.13 |  |  |  | 10.01.17 | 3
229 | Air Blower 16-B | 09U1G16B | ETPMCC/1F3 | Bharat Bijiee | 75/55 | [12 empty] | 0
230 | Air Blower | 09U1G17 | ETPMCC/5F4 | Bharat Bijiee | 25/18.5 | 03.02.09 |  |  | 03.02.09 | [7 empty] | 16.02.17 | 2
231 | Heat Exchanger Feed Pump-A | 09U1G1A | ETPMCC/6R2 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
232 | Heat Exchanger Feed Pump-B | 09U1G1B | ETPMCC/5R6 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
233 | C-MEM A Water Transfer Pump | 09U1G20 | ETPMCC/6F1 | GRUNDFOS | 2/1.5 | 02.11.0911.04.11 |  |  | 02.11.09 |  | 11.04.11 |  |  |  | 08.07.15 |  |  | 3
234 | Process Water Transfer pump | 09U1G21 | ETPMCC/9R2 | Bharat Bijiee | 7.5/5.5 | [12 empty] | 0
235 | C-MEM B Water Transfer Pump | 09U1G22 | ETPMCC/6F2 | GRUNDFOS | 2/1.5 | 12.09.09 |  |  | 12.09.09 | [8 empty] | 1
236 | C-MEM A Backwash Pump | 09U1G23 | ETPMCC/5F3 | Bharat Bijiee | 15/11 | 22.01.12 | [5 empty] | 22.01.12 | [5 empty] | 1
237 | C-MEM B Backwash Pump | 09U1G24 | ETPMCC/7F1 | Bharat Bijiee | 15/11 | [12 empty] | 0
238 | RO Cartridge feed Pump | 09U1G25 | ETPMCC/8F4 | Bharat Bijiee | 7.5/5.5 | [11 empty] | 05.02.17 | 1
239 | RO High Pr. Pump | 09U1G26 | ETPMCC/7F2 | GRUNDFOS | 15/11 | [12 empty] | 0
240 | RO Permeate Transfer Pump | 09U1G27 | ETPMCC/8R3 | GRUNDFOS | 3.1/2.3 | [12 empty] | 0
241 | RO Cleaning Soln. Pump | 09U1G28 | ETPMCC/9R3 | GRUNDFOS | 5.5/4 | [12 empty] | 0
242 | Lime Dosing Pump- A | 09U1G29A | ETPMCC/4F1 | Bharat Bijiee | .5/.37 | [12 empty] | 0
243 | Lime Dosing Pump- B | 09U1G29B | ETPMCC/4F2 | Bharat Bijiee | .5/.37 | [12 empty] | 0
244 | Lamella Feed Pump A | 09U1G2A | ETPMCC/4F4 | Bharat Bijiee | .5/.37 | [12 empty] | 0
245 | Lamella Feed Pump B | 09U1G2B | ETPMCC/9F5 | Bharat Bijiee | .5/.37 | [12 empty] | 0
246 | Flash Mixer 4A | 09U1G3 | ETPMCC/4F5 | Bharat Bijiee | .5/.37 | [12 empty] | 0
247 | Lime Tank Agitator | 09U1G30 | ETPMCC/3R5 | Bharat Bijiee | .5/.37 | [12 empty] | 0
248 | FeCl3Dosing Tank Agitator | 09U1G32 | ETPMCC/7F4 | Bharat Bijiee | .16/.12 | 13.08.09 |  |  | 13.08.09 | [8 empty] | 1
249 | Polymer Dosing tank Agitator | 09U1G35 | ETPMCC/3R2 | Bharat Bijiee | .5/.37 | [12 empty] | 0
250 | Acid Doasing Pump B | 09U1G36B | ETPMCC/8F1 | Bharat Bijiee | .5/.37 | 05.04.07 | 05.04.07 | [10 empty] | 1
251 | Deoiling Polymer tank Agitator | 09U1G38 | ETPMCC/9R1 | Bharat Bijiee | .5/.37 | [12 empty] | 0
252 | PAC Dosing Pump | 09U1G39 | ETPMCC/3R4 | Bharat Bijiee | .5/.37 | [12 empty] | 0
253 | Flocculator Tank Agitator 4B | 09U1G4 | ETPMCC/4R3 | Bharat Bijiee | .5/.37 | [12 empty] | 0
254 | Nutrient Dosing Pump | 09U1G41 | ETPMCC/3R1 | Bharat Bijiee | .5/.37 | [12 empty] | 0
255 | Nutrient Dosing tank Agitator | 09U1G42 | ETPMCC/4F3 | Bharat Bijiee | .5/.37 | [12 empty] | 0
256 | NaOCl Dosing Pump | 09U1G43 | ETPMCC/5F1 | Bharat Bijiee | 10/7.5 | [12 empty] | 0
257 | Organic Clining Doasing Pump | 09U1G44 | ETPMCC/5F2 | Bharat Bijiee | 12.5/9.3 | [12 empty] | 0
258 | Organic Clining tank Agitator | 09U1G45 | ETPMCC/6R3 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
259 | Cleaning Soln. Tank Agitator | 09U1G51 | ETPMCC/4R5 | Bharat Bijiee | 1/.75 | [12 empty] | 0
260 | Dewatering Polymer Dosing Pump | 09U1G52 | ETPMCC/9F6 | Bharat Bijiee | .5/.37 | [12 empty] | 0
261 | Dewatering Polymer Tank Agitator | 09U1G53 | ETPMCC/9F2 | Bharat Bijiee | .5/.37 | [12 empty] | 0
262 | NaOH Dosing Pump | 09U1G54 | ETPMCC/9F3 | Bharat Bijiee | .5/.33 | [12 empty] | 0
263 | NaOH Tank Agitator | 09U1G55 | ETPMCC/7F5 | Bharat Bijiee | .16/.12 | [12 empty] | 0
264 | DAF FeedPump - A | 09U1G5A | ETPMCC/7R1 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
265 | DAF FeedPump - B | 09U1G5B | ETPMCC/7R4 | Bharat Bijiee | 1.5/1.1 | [12 empty] | 0
266 | Flash Mixer Tank Agitator 7A | 09U1G6 | ETPMCC/9F1 | Bharat Bijiee | .5/.37 | 17.07.09 |  |  | 17.07.09 | [8 empty] | 1
267 | Flocculator Tank Agitator 7B | 09U1G7 | ETPMCC/9F4 | Bharat Bijiee | .75/.55 | 03.08.09 |  |  | 03.08.09 | [8 empty] | 1
268 | Air compressor | 09U1G8 | ETPMCC/5R1 | Bharat Bijiee | 1/.75 | [12 empty] | 0
269 | DAF High Pr. Pump | 09U1G9 | ETPMCC/8R4 | GRUNDFOS | 4.2/3 | 22.05.10/30.03.1003.03.11 |  |  |  | 22.05.10/30.03.10 | 03.03.11 | [6 empty] | 2
270 | ETP Scrubber | 09U1G9D |  |  | 0.75kw | 18.08.13 | [6 empty] | 18.08.13 |  |  |  |  | 1
271 | Effluent transfer pump | 09U2G1A | M01/BUS-B/20F1 | SIEMENS | 20/15 | [12 empty] | 0
272 | F.D.Fan | 10G01A | M01/HYMCC/2R3 | Bharat Bijiee | 100/75 | 29.05.1203.04.14 | [5 empty] | 29.05.12 |  | 03.04.14 |  |  |  | 2
273 | F.D.Fan | 10G01B | M01/HYMCC/3R3 | Bharat Bijiee | 100/75 | 28.05.1228.03.14/03.04.14 | [5 empty] | 28.05.12 |  | 28.03.14/03.04.14 |  | 03.03.16/04.03.16 |  | 3
274 | F.D.Fan | 10G01C |  | Crompton Greaves | 215/160 | 08.04.0824.12.1118.12.1204.02.13 |  | 08.04.08 |  |  | 24.12.11 | 18.12.12 | 04.02.13 |  |  |  | 06.02.17 | 5
275 | Recycle H2 Compressor | 10G02 | M01/HYMCC/2F1 | Bharat Bijiee | 12.5/9.3 | 08.01.0923.02.14 |  |  | 08.01.09 |  |  |  |  | 23.02.14 |  | 13.08.16 |  | 3
276 | Naptha feed pump | 10G03A | M01/HYMCC/2R2 | BBL | 20/15 | 20.05.09 |  |  | 20.05.09 | [8 empty] | 1
277 | Naptha feed pump | 10G03B | M01/HYMCC/3R1 | BBL | 20/15 | 12.03.09 |  |  | 12.03.09 | [8 empty] | 1
278 | BWF pumps | 10G04A | M01/HYMCC/2F4 | BBL | 30/22 | [11 empty] | 07.02.17 | 1
279 | BWF pumps | 10G04B | M01/HYMCC/3F3 | BBL | 30/22 | [11 empty] | 09.02.17/ 27.03.17 | 2
280 | Naptha condensate pump | 10G05 | M01/BUS-C/35F3 | Kirloskar | 3/2.2 | [12 empty] | 0
281 | TNP Dosing pump | 10U2G1 | M01/HYMCC/1R1 | BBL | .5/.37 | 01.09.09/05.03.09 |  |  | 01.09.09/05.03.09 | [5 empty] | 10.10.2015 |  |  | 2
282 | Na2S Dosing pump | 10U2G2 | M01/HYMCC/4R1 | BBL | .5/.37 | 21.10.0931.08.13 |  |  | 21.10.09 |  |  |  | 31.08.13 |  |  |  |  | 2
283 | Mixer for phosphat tank | 10U2G3 | M01/HYMCC/3F2 | BBL | 1/.75 | [12 empty] | 0
284 | Mixer for Hydrozen tank | 10U2G4 | M01/HYMCC/2F3 | BBL | 1/.75 | [12 empty] | 0
285 | Alcohol feed pump | 14G01A | MCC121/2F2 | SIEMENS | 12.5/9.3 | [12 empty] | 0
286 | Alcohol feed pump | 14G02A | MCC121/4F4 | SIEMENS | 12.5/9.3 | 20.07.11 |  |  |  |  | 20.07.11 | [6 empty] | 1
287 | Alcohol feed pump | 14G03A | MCC121/2F4 | SIEMENS | 12.5/9.3 | [12 empty] | 0
288 | Storage tank area | 14P01A |  |  | 15KW | 08.10.13 | [6 empty] | 08.10.13 |  |  |  |  | 1
289 | Caustic unloading pump | 14P02A |  |  | 9.3 | [12 empty] | 0
290 | Caustic unloading pump - 2 | 14P02B |  |  | 3.7 | [12 empty] | 0
291 | Caustic unloading pump - 3 | 14P04A |  |  | 7.5 | [12 empty] | 0
292 | Caustic soda transfer pump from PIT | 14P04B |  |  | 9.3 | [12 empty] | 0
293 | Slop sump pump | 14P05 |  |  | 3.7 | [12 empty] | 0
294 | Hot well pump | 20P01 |  |  | 3.7 | [12 empty] | 0
295 | Cold well pump | 20P02A |  |  | 9.3 | [12 empty] | 0
296 | Cold well pump | 20P02B |  |  | 9.3 | [12 empty] | 0
297 | Cooling water pump-1 | 20P03A |  |  | 110 | [10 empty] | 20.05.2016 |  | 1
298 | Cooling water pump-2 | 20P03B |  |  | 110 | [10 empty] | 12.05.2016 |  | 1
299 | Cooling water pump-3 | 20P04A |  |  | 37 | 17.09.0707.12.08 | 17.09.07 | 07.12.08 | [9 empty] | 2
300 | Cooling water pump-4 | 20P05A |  |  | 18.5kw | 09.12.08 |  | 09.12.08 | [9 empty] | 1
301 | Condensate transfer pump B | 22P1A |  |  | 2.2 | [12 empty] | 0
302 | Condensate transfer pump A | 22P1B |  |  | 2.2 | [12 empty] | 0
303 | Effluent transfer pump | 23P1 |  |  | 7.5 | JULY,1318.09.14 | [6 empty] | JULY,13 | 18.09.14 |  |  |  | 2
304 | ETP PUMP-2 | 23P2 |  |  | 15 | 22.03.13/03.05.1302.02.14 | [6 empty] | 22.03.13/03.05.13 | 02.02.14 | 30.05.15 |  |  | 3
305 | NEW VP NEAR VP-27,K3 | 6TH FLR |  | SIEMENS | 11 | [12 empty] | 0
306 | Agitator | A-651A | MCC121/2F5 | suzhou motor | 1.1 kw | [12 empty] | 0
307 | Agitator | A-651B | MCC121/3F3 | suzhou motor | 1.1 kw | [12 empty] | 0
308 | Agitator | A-651C |  | suzhou motor | 1.1 kw | [12 empty] | 0
309 | Mixer | A-704 | 111/5F1 | Crompton greaves | 3/2.2 | [12 empty] | 0
310 | BATCH BLEACHER AGITATOR | AG-7106 |  |  | 3.7 | [12 empty] | 0
311 | ATFD STIRRER | AG-7110 |  |  | 7.5 | [12 empty] | 0
312 | CGS Agitator motor | AGITATOR | Splitting MCC/2F3 | SCORCH | 3.7 | installed in 11 |  |  |  |  | installed in 11 |  |  |  | 16.09.2015 |  |  | 2
313 | blower | BDG-1 |  |  |  | 26.12.08 |  | 26.12.08 | [7 empty] | 09.01.2016 |  | 2
314 | Recycle compressor | C-103A | E 04 | Bhart Bijali | 3.7 | [12 empty] | 0
315 | Recycle compressor | C-103B | E 05 | Bhart Bijali | 3.7 | [12 empty] | 0
316 | cooling water pump -1 | c-301 | NEW-FLK-1F4 | kirloskar | 15/11 | 21.05.0916.02.12 |  |  | 21.05.09 |  |  | 16.02.12 |  |  | 28.01.15 |  |  | 3
317 | cooling water pump -2 | c-302 |  | kirloskar | 15/11 | [12 empty] | 0
318 | cooling water pump -3 | c-303 | 3F2 | kirloskar | 15/11 | 10.07.0819.10.12 |  | 10.07.08 |  |  |  | 19.10.12 |  |  | 07.07.15 |  |  | 3
319 | PUMP | C-401 | NEW-FLK | kirloskar | 15/11 | [12 empty] | 0
320 | PUMP | C-402 | NEW-FLK | kirloskar | 15/11 | 15.07.14 | [7 empty] | 15.07.14 |  | 12.01.2016 |  | 2
321 | PUMP | C-403 | NEW-FLK | kirloskar | 15/11 | 06.04.1030.06.14 |  |  |  | 06.04.10 |  |  |  | 30.06.14 | 04.12.2015 |  |  | 3
322 | Post cooler chain conveyor | C-901 |  | SIEMENS | 7.5/5.5 | [12 empty] | 0
323 | Rotoform Ist pastillator | C-902 |  | Sew Eurodrive | 3/2.2 | [12 empty] | 0
324 | Steel belt conveyor | C-903 |  | Sew Eurodrive | 10/7.5 | [12 empty] | 0
325 | conveyor No 1 | C-904 |  | Crompton greaves | 2/1.5 | [12 empty] | 0
326 | conveyor No 2 (wood steeper) | C-905 |  | Bonfiglioli Group | 1/.75 | [12 empty] | 0
327 | conveyor No 3(metal detector) | C-906 |  | Crompton greaves | 1/0.75 | [12 empty] | 0
328 | Conveyer no.4(Bag rejector) | C-907 |  | Bharat bijlee | .37/.5 | [12 empty] | 0
329 | Clean condensate Pump | CD-100 |  |  | 2.2kw | 19.11.12 | [5 empty] | 19.11.12 | [5 empty] | 1
330 | WATER CHILLING PLANT-1 | CH-7000A |  |  | 55 | [12 empty] | 0
331 | WATER CHILLING PLANT-2 | CH-7000B |  |  | 55 | [12 empty] | 0
332 | CT FAN-1 JUTASAMA | CT FAN-1 | JSMCC/4R5 | NBE | 11 | [12 empty] | 0
333 | CT FAN-2 JUTASAMA | CT FAN-2 | UMCC/4R3 | NBE | 11 | 09.06.201220.02.14 |  |  |  |  | 09.06.2012 |  |  | 20.02.14 |  |  |  | 2
334 | Cooling tower fan | CT-903A-F | 112/2F4 | Siemens | 20/15 | [12 empty] | 0
335 | Cooling tower fan | CT-903B-F | 112/3F3 | Siemens | 20/15 | 16.12.13 | [6 empty] | 16.12.13 |  |  |  |  | 1
336 | Cooling tower fan | CT-903C-F | 112/2F4 | Siemens | 20/15 | 03.04.12/23.09.12 | [5 empty] | 03.04.12/23.09.12 | [5 empty] | 1
337 | Hotwell pump | D-1-1 | k3 / 1R1 | HINDUSTAN | 40/30 | 02.04.1125.05.12/11.11.1206.03.1307.01.14/18.04.14/206.3 overhauled motor given to D-1-1 on20.06.14 |  |  |  |  | 02.04.11 | 25.05.12/11.11.12 | 06.03.13 | 07.01.14/18.04.14/206.3 overhauled motor given to D-1-1 on20.06.14 | 09.02.15 |  | 10.01.17 | 6
338 | Hotwell pump | D-1-2 | k3 / 2R1 | HINDUSTAN | 40/30 | 11.04.0919.04.12/25.05.1228.02.14 |  |  | 11.04.09 |  |  | 19.04.12/25.05.12 |  | 28.02.14 |  |  |  | 3
339 | 1st Treated Sweet Water Filter Press | F/P-I | Precon MCC/5F1 | CG | 2.2 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
340 | 2nd Treated Sweet Water Filter Press | F/P-II | Precon MCC | CG | 1.5 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
341 | ID fan | F-101 | E 01 | ABB | 30/22 | 07.06.11/20.07.1118.07.14 |  |  |  |  | 07.06.11/20.07.11 |  |  | 18.07.14 |  | 19.09.16 |  | 3
342 | FD fan | F-102 | E 12 | ABB | 10/7.5 | 20.11.1109.07.14 |  |  |  |  | 20.11.11 |  |  | 09.07.14 |  | 21.09.16 |  | 3
343 | Flaker | FL-101 | PILOT MCC/1F4 | CG | 0.75/1 | installed in 10 |  |  |  | installed in 10 | [7 empty] | 1
344 | Dosing pump | G11B M 01 | PMCC/18F1 | Bhart Bijali | 3/2.2 | [12 empty] | 0
345 | Dosing pump | G20 M01 | PMCC/18F2 | Bhart Bijali | 0.5/0.37 | [12 empty] | 0
346 | Atlas copco | 06G(75) |  |  |  | 17.08.12 | [5 empty] | 17.08.12 | [5 empty] | 1
347 | Hot well to Cooling tower pump | O1G19B | PMCC-37R2 | Bharat Bijiee | 20/15 | [12 empty] | 0
348 | Water Feed Pump | P-205A | Splitting MCC/2F2 | BBL | 2.2 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
349 | Water Feed Pump | P-205B | Splitting MCC/2F3 | BBL | 3.75 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
350 | Fatty Acid Circulation Pump | P-206A | Splitting MCC/3F4 | SIEMENS | 15 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
351 | Fatty Acid Circulation Pump | P-206B | Splitting MCC/3F5 | SIEMENS | 15 | installed in 1118.10.1320.09.14 |  |  |  |  | installed in 11 |  | 18.10.13 | 20.09.14 |  |  |  | 3
352 | Fat Circulation Pump | P-208A | Splitting MCC/2F2 | CG | 7.5 | installed in 11 |  |  |  |  | installed in 11 |  |  |  | 02.03.15 |  |  | 2
353 | Fat Circulation Pump | P-208B | Splitting MCC/2F3 | CG | 7.5 | installed in 1109.03.2014 |  |  |  |  | installed in 11 |  | 09.03.2014 |  |  |  |  | 2
354 | Collected oil transfer Pump | P-209 | Splitting MCC/2F3 | BBL | 3.7 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
355 | High Pressure Fat / Water Feed Pump | P-602A | Precon MCC/4F5 | Laxmi hydraulics pvt.ltd | 3.7 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
356 | High Pressure Fat / Water Feed Pump | P-602B | Precon MCC/4F2 | SIEMENS | 2.2 | Installed in 2012 | [5 empty] | Installed in 2012 |  |  |  | 13.09.16 |  | 2
357 | Crude Sweet Water Transfer Pump | P-604A | Precon MCC | ABB | 3.7 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
358 | Crude Sweet Water Transfer Pump | P-604B | Precon MCC | BBL | 3.7 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
359 | Decanted oil transfer pump | P-605 | Precon MCC | BBL | 3.7 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
360 | Fatty Acid Circulation Pump | P-606 | Precon MCC/5F3 | Siemens | 15 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
361 | Fat Circulation Pump | P-607 | Precon MCC/5F4 | Siemens | 15 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
362 | Fat Circulation Pump | P-608 | Precon MCC/5F5 | Siemens | 15 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
363 | Skimmed oil transfer pump | P-610 | Precon MCC/4F3 | SIEMENS | 3.7 | Installed in 2012 | [5 empty] | Installed in 2012 | [5 empty] | 1
364 | Bottom circulation pump | P-765 | Splitting MCC/3F1 | ABB | 11 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
365 | Vaccum Pump | P-795 | Splitting MCC/2F2 | siemens | 7.5 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
366 | Condensate Transfer Pump | P-8001A | Precon MCC/3F4 | BBL | 5.5 | 23.09.1223.08.13 | [5 empty] | 23.09.12 | 23.08.13 |  | 06.08.2015 |  |  | 3
367 | Condensate Transfer Pump | P-8001B | Precon MCC/3F5 | BBL | 5.5 | installed in 12 | [5 empty] | installed in 12 |  |  |  |  | 06.03.17 | 2
368 | High Pressure Fat Feed Pump | P-201 | Splitting MCC/1F3 | siemens | 30 | installed in 11 |  |  |  |  | installed in 11 | [5 empty] | 14.01.17 | 2
369 | P-201 MAIN MOTOR COOLING FAN | P-201 | Splitting MCC/1F3 | VBM ENTR | 0.17 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
370 | High Pressure Fat / Water Feed Pump | P-202 | Splitting MCC/1F4 | siemens | 30 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
371 | P-202 MAIN MOTOR COOLING FAN | P-202 | Splitting MCC/1F4 | VBM ENTR | 0.17 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
372 | Water Charge Pump. | P-203 | Splitting MCC/1F5 | siemens | 22 | installed in 11 |  |  |  |  | installed in 11 |  |  |  |  | 03.10.16 |  | 2
373 | P-203 MAIN MOTOR COOLING FAN | P-203 | Splitting MCC/1F5 | VBM ENTR | 0.135 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
374 | FAF BLOWER | P-1000 |  |  | 110 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
375 | AUX.AIR FAN 2 | P-1001 |  |  | 2.2 | installed in 1209.03.13/03.06.13 | [5 empty] | installed in 12 | 09.03.13/03.06.13 |  |  |  |  | 2
376 | AUX.AIR FAN 1 | P-1002 |  |  | 1.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
377 | GULLOTINE DAMPER G5_01 | P-1003 |  |  |  | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
378 | GULLOTINE DAMPER G5_02 | P-1004 |  |  |  | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
379 | GULLOTINE DAMPER G5_03 | P-1005 |  |  |  | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
380 | SAF GD-01 | P-1006 |  |  | 4 | 27.08.12 | [5 empty] | 27.08.12 | [5 empty] | 1
381 | SAF GD-02 | P-1007 |  |  | 4 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
382 | SAF GD-03 | P-1008 |  |  | 4 | installed in 1216.12.14/18.12.14 | [5 empty] | installed in 12 |  | 16.12.14/18.12.14 |  | 29.11.16 |  | 3
383 | SAF FD-01 | P-1009 |  |  | 7.5 | installed in 1229.05.14 | [5 empty] | installed in 12 |  | 29.05.14 |  |  |  | 2
384 | Naphta feed pump | P-100A1 | E 10 | Bhart Bijali | 5.5 | [12 empty] | 0
385 | Naphta feed pump | P-100A2 | E 11 | Bhart Bijali | 5.5 | [12 empty] | 0
386 | Naphta feed pump | P-100B1 | E 13 | Bhart Bijali | 5.5 | [12 empty] | 0
387 | Naphta feed pump | P-100B2 | E 14 | Bhart Bijali | 5.5 | [12 empty] | 0
388 | Transfer pump | P-101 | PILOT MCC/2F4 | CG | 2.2/3 | installed in 10 |  |  |  | installed in 10 | [7 empty] | 1
389 | High pressure pump | P-101 | VFD PANEL | Siemens | 110 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
390 | BOILER FEED WATER PUMP-1 | P-1010A |  |  | 75 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
391 | BOILER FEED WATER PUMP-2 | P-1010B |  |  | 75 | installed in 1227.05.1308.03.14 | [5 empty] | installed in 12 | 27.05.13 | 08.03.14 |  |  |  | 3
392 | THERMIC FLUID PUMP-1 | P-1011A |  |  | 110 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
393 | THERMIC FLUID PUMP-2 | P-1011B |  |  | 110 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
394 | COOLING WATER PUMP-1 | P-1012A |  |  | 30 | installed in 12 | [5 empty] | installed in 12 |  |  | 27.05.15/11.07.15 | 13.05.2016 & 28.11.16 |  | 3
395 | COOLING WATER PUMP-2 | P-1012B |  |  | 30 | installed in 12 | [5 empty] | installed in 12 |  |  |  | 28.11.16 |  | 2
396 | COOLING WATER PUMP-3 | P-1012C |  |  | 30 | installed in 12 | [5 empty] | installed in 12 |  |  | 26.05.15 | 29.11.16 |  | 3
397 | CHILLED WATER PUMP-1 | P-1013A |  |  | 30 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
398 | CHILLED WATER PUMP-2 | P-1013B |  |  | 30 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
399 | CHILLED WATER PUMP-3 | P-1013C |  |  | 30 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
400 | STARTUP VENT S24 | P-1014A |  |  |  | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
401 | STEAM SUPPLY S25 | P-1014B |  |  |  | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
402 | HOT WATER PUMP-1 | P-1015A |  |  | 18.5 | 07.12.1228.12.14 | [5 empty] | 07.12.12 |  | 28.12.14 |  |  | 16.01.17/04.02.17 | 4
403 | HOT WATER PUMP-2 | P-1015B |  |  | 18.5 | installed in 12 | [5 empty] | installed in 12 |  |  |  | 27.10.16 |  | 2
404 | CT FAN-1 | P-1016A |  |  | 15 | installed in 1219.07.14 | [5 empty] | installed in 12 |  | 19.07.14 | 26.08.2015 |  | 16.03.17 | 4
405 | CT FAN-2 | P-1016B |  |  | 15 | installed in 1222.08.14/04.11.2014 | [5 empty] | installed in 12 |  | 22.08.14/04.11.2014 | 27.08.2015 |  | 15.02.17 | 4
406 | COOLING WATER GT PUMP 1 | P-1017A |  |  | 7.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
407 | COOLING WATER GT PUMP 2 | P-1017B |  |  | 7.5 | installed in 12 | [5 empty] | installed in 12 |  |  |  | 30.11.16 |  | 2
408 | AIR COMPRESSOR-A | P-1018A |  |  | 7.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
409 | AIR COMPRESSOR-B | P-1018B |  |  | 7.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
410 | LP DOSING PUMP-1 | P-1019A |  |  | 0.37 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
411 | LP DOSING PUMP-2 | P-1019B |  |  | 0.37 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
412 | LP DOSING AGITATOR | P-1019C |  |  | 0.37 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
413 | BFW pump | P-101A | E 02 | Bhart Bijali | 18.5 | 05.03.12 | [5 empty] | 05.03.12 | [5 empty] | 1
414 | BFW pump | P-101B | E 03 | Bhart Bijali | 18.5 | 30.04.09/04.12.0924.12.1128.01.12 |  |  | 30.04.09/04.12.09 |  | 24.12.11 | 28.01.12 | [5 empty] | 3
415 | High pressure pump | P-102 | VFD PANEL | Siemens | 110 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
416 | HP DOSING PUMP-1 | P-1020A |  |  | 0.75 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
417 | HP DOSING PUMP-2 | P-1020B |  |  | 0.75 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
418 | HP DOSING AGITATOR | P-1020C |  |  | 0.75 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
419 | MAKEUP WATER PUMP | P-1021 |  |  | 0.55 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
420 | Hot oil circulation pump | P-103 | PILOT MCC/1F3 | CG | 0.75/1 | installed in 10 |  |  |  | installed in 10 | [7 empty] | 1
421 | High pressure pump | P-103 | VFD PANEL | Siemens | 90 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
422 | Water ring vacuum pump | P-104 | PILOT MCC/2F5 | PEW | 3.7/5 | installed in 10 |  |  |  | installed in 10 | [7 empty] | 1
423 | Feed pump Oil to V- 101 | P-104A | JSMCC/4F5 | Siemens | 30 | [12 empty] | 0
424 | Feed pump Oil to V- 101 | P-104B | JSMCC/2F3 | Siemens | 30 | [12 empty] | 0
425 | Feed pump Jutasama | P-104D |  |  |  | 07.04.12 | [5 empty] | 07.04.12 |  |  | 16.01.15 |  |  | 2
426 | Cooling water transfer pump | P-105 | PILOT MCC/1F7 | CG | 2.2/3 | installed in 10 |  |  |  | installed in 10 | [7 empty] | 1
427 | Water Feed Pump | P-105A | JSMCC/4F6 | Siemens | 7.5 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
428 | Water Feed Pump | P-105B | JSMCC/2F2 | Siemens | 7.5 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
429 | Split Fatty Acid Transfer Pump | P-106A | JSMCC/2F2 | Siemens | 45 | 17.12.11 |  |  |  |  | 17.12.11 | [6 empty] | 1
430 | Split Fatty Acid Transfer Pump | P-106B | JSMCC/2R4 | Siemens | 45 | 24.12.11 |  |  |  |  | 24.12.11 | [6 empty] | 1
431 | Crude OIl CIrculation Pump | P-107A | JSMCC/2R5 | Siemens | 11 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
432 | Crude OIl CIrculation Pump | P-107B | JSMCC/2R1 | Siemens | 11 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
433 | Collected oil transfer pump | P-109 | JSMCC/2F7 | Siemens | 3.7 | [12 empty] | 0
434 | E-103 thermic fluid circulation pump | P-14A | K3/ 2F2 | ABB | 7.5/5.5 | 14.08.09 |  |  | 14.08.09 | [8 empty] | 1
435 | E-103 thermic fluid circulation pump | P-14B | K3 / 2F3 | ABB | 7.5/5.5 | 14.08.0908.03.14 |  |  | 14.08.09 |  |  |  |  | 08.03.14 |  |  |  | 2
436 | Thermic fluid circulation pump | P-2601A |  | Siemens | 75/55 | [12 empty] | 0
437 | Thermic fluid circulation pump | P-2601B |  | Siemens | 75/55 | [12 empty] | 0
438 | Water ring vacuum pump | P-27A | k3 / 1R2 | ABB | 15/11 | 09.11.09 |  |  | 09.11.09 | [5 empty] | 08.02.15 |  | 02.02.17 | 3
439 | K-3 Reboiler circulation pump | P-29A | K3 / 3F4 | KIR | 20/15 | 09.12.1111.11.12 |  |  |  |  | 09.12.11 | 11.11.12 | [5 empty] | 2
440 | K-3 Reboiler circulation pump | P-29B | K3 / 3F5 | CG | 20/15 | 09.11.0929.05.14 |  |  | 09.11.09 |  |  |  |  | 29.05.14 |  |  |  | 2
441 | C6/C8 transfer pump-1 | P-303A | 102A/1F3 | Siemens | 3/2.2 | [12 empty] | 0
442 | C6/C8 transfer pump-2 | P-303B | 102A/1F4 | Siemens | 3/2.2 | 03.01.12 | [5 empty] | 03.01.12 | [5 empty] | 1
443 | C10/12 transfer pump-1 | P-304A | 102A/1F5 | Siemens | 7.5/5.5 | [12 empty] | 0
444 | C10/12 transfer pump-2 | P-304B | 102A/3F5 | Siemens | 7.5/5.5 | [12 empty] | 0
445 | C8/C10 transfer pump-1 | P-305A | 102A/4F2 | Siemens | 10/7.5 | 21.09.12 | [5 empty] | 21.09.12 | [5 empty] | 1
446 | C8/C10 transfer pump-2 | P-305B | 102A/2R3 | Siemens | 10/7.5 | [12 empty] | 0
447 | C12/C14 transfer pump-1 | P-306A | 102A/2F1 | Siemens | 15/11 | [12 empty] | 0
448 | C12/C14 transfer pump-2 | P-306B | 102A/4R1 | Siemens | 15/11 | [9 empty] | 30.05.15/05.06.15 |  |  | 1
449 | Reboiler circulation pump-1 | P-307A | 102A/4F3 | Siemens | 20/15 | 23.09.14 | [7 empty] | 23.09.14 |  | 07.02.2016 | 22.03.17 | 3
450 | Reboiler circulation pump-2 | P-307B | 102A/5F3 | Siemens | 20/15 | 14.08.12 | [5 empty] | 14.08.12 |  |  | 25.04.15 |  |  | 2
451 | Reboiler circulation pump-1 | P-308A | 102A/4F4 | Siemens | 25/18.5 | [12 empty] | 0
452 | Reboiler circulation pump-2 | P-308B | 102A/5F4 | Siemens | 25/18.5 | [12 empty] | 0
453 | Bottom product transfer pump-1 | P-309A | 102A/3F2 | Siemens | 3/2.2 | 03.02.0905.08.10 |  |  | 03.02.09 | 05.08.10 | [7 empty] | 2
454 | Bottom product transfer pump-2 | P-309B | 102A/3F1 | Siemens | 3/2.2 | 23.11.0708.09.0916.03.10/24.08.10 | 23.11.07 |  | 08.09.09 | 16.03.10/24.08.10 |  |  |  |  | 26.04.2015 | 02.02.2016 |  | 5
455 | K-3 bottom product transferring pump | P-30A | k3 / 2R3 | CG | 20/15 | 18.06.13 | [6 empty] | 18.06.13 |  |  | 17.09.16 |  | 2
456 | K-3 bottom product transferring pump | P-30B | k3 / 2R2 | CG | 10/7.5 | 22.03.10/07.04.1014.12.13 |  |  |  | 22.03.10/07.04.10 |  |  | 14.12.13 |  | 09.02.15/01.06.15 |  |  | 3
457 | K-3 bottom product transferring pump | P-30C | K3/ 3R5 | ABB | 7.5/5.5 | 09.11.09 |  |  | 09.11.09 | [8 empty] | 1
458 | Bottom product transfer pump-1 | P-310A | 102A/3R1 | Siemens | 7.5/5.5 | [12 empty] | 0
459 | Bottom product transfer pump-2 | P-310B | 102A/2R1 | Siemens | 7.5/5.5 | 02.10.0728.07.0915.03.13/16.12.13 | 02.10.07 |  | 28.07.09 |  |  |  | 15.03.13/16.12.13 |  |  |  |  | 3
460 | Hot oil circulation pump-1 | P-311A | 102A/5R2 | Siemens | 20/15 | 07.04.14/14.12.14 | [7 empty] | 07.04.14/14.12.14 |  |  |  | 1
461 | Hot oil circulation pump-2 | P-311B | 102A/4R3 | Siemens | 20/15 | [12 empty] | 0
462 | Hot oil circulation pump-1 | P-312A | 102A/2F4 | Siemens | 25/18.5 | [12 empty] | 0
463 | Hot oil circulation pump-2 | P-312B | 102A/5F5 | Siemens | 25/18.5 | [11 empty] | 22.03.17 | 1
464 | Dryer circulation pump-1 | P-313A | 102A/5R3 | Siemens | 25/18.5 | [12 empty] | 0
465 | Dryer circulation pump-2 | P-313B | 102A/1R4 | Siemens | 25/18.5 | [12 empty] | 0
466 | LE transfer pump-1 | P-314A | 102A/4F1 | Siemens | 3/2.2 | [12 empty] | 0
467 | LE transfer pump-2 | P-314B | 102A/5F1 | Siemens | 3/2.2 | [12 empty] | 0
468 | SFA feed pump-1 | P-317A | 102A/2F2 | Siemens | 5/3.7 | [12 empty] | 0
469 | SFA feed pump-2 | P-317B | 102A/2F3 | Siemens | 5/3.7 | [12 empty] | 0
470 | Hot oil dooster pump-1 | P-318A | 102A/2R2 | Siemens | 7.5/5.5 | 04.04.0711.11.200814.10.1122.09.14 | 04.04.07 |  | 11.11.2008 |  | 14.10.11 |  |  | 22.09.14 | 12.02.15 |  |  | 5
471 | Hot oil dooster pump-2 | P-318B | 102A/1R2 | Siemens | 7.5/5.5 | 21.110702.09.0910.04.14 | 21.1107 |  | 02.09.09 |  |  |  |  | 10.04.14 |  |  | 29.03.17 | 4
472 | E-13 Condensate transferring pump | P-31A | k3 / 1F3 | ABB | 7.5/5.5 | 09.11.09 |  |  | 09.11.09 | [8 empty] | 1
473 | E-13 Condensate transferring pump | P-31B | k3 / 1F4 | ABB | 7.5/5.5 | 09.11.09 |  |  | 09.11.09 | [8 empty] | 1
474 | Oil circulation pump-1 | P-320A | 102A/5R4 | Siemens | 30/22 | 18.03.1118.10.12 |  |  |  |  | 18.03.11 | 18.10.12 | [5 empty] | 2
475 | Oil circulation pump-2 | P-320B | 102A/5R5 | Siemens | 30/22 | 30.12.0829.05.013 |  | 30.12.08 |  |  |  |  | 29.05.013 |  |  | 12.03.16 |  | 3
476 | Direct CW pump-1 | P-322A | 112/4F3 | Siemens | 20/15 | 15.01.14 | [7 empty] | 15.01.14 | 06.07.2015 |  |  | 2
477 | Direct CW pump-2 | P-322B | 112/2R2 | Siemens | 20/15 | [12 empty] | 0
478 | Effluent transfer pump | P-323A | 102A/3F3 | Siemens | 12/9.3 | 11.02.11/21.02.11/14.03.11 |  |  |  |  | 11.02.11/21.02.11/14.03.11 | [6 empty] | 1
479 | Effluent transfer pump | P-323B | 102A/3F4 | Kirloskar | 5/3.7 | 12.08.1206.01.14 | [5 empty] | 12.08.12 |  | 06.01.14 |  |  |  | 2
480 | Condensate pump-1 | P-324A | 102A/5F2 | Siemens | 3/2.2 | 04.02.0826.04.11 |  | 04.02.08 |  |  | 26.04.11 | [6 empty] | 2
481 | Condensate pump-2 | P-324B | 102A/4R2 | Siemens | 3/2.2 | [12 empty] | 0
482 | Cooling water pump-1 | P-326A | 102A/2R4 | Siemens | 20/15 | [12 empty] | 0
483 | Cooling water pump-2 | P-326B | 102A/7F3 | Siemens | 20/15 | [12 empty] | 0
484 | thermic fluid transfer pump | P-327 | [15 empty] | 0
485 | Oil transfer pump to storage tank | P-327A | 102A/7F1 | Siemens | 5/3.7 | [12 empty] | 0
486 | M/D transferring pump | P-32A | k3 / 2R4 | ABB | 12.5/9.3 | 26.02.11 |  |  |  |  | 26.02.11 | [6 empty] | 1
487 | M/D transferring pump | P-32B | k3 / 2R5 | CG | 20/15 | 07.12.11 |  |  |  |  | 07.12.11 | [6 empty] | 1
488 | M/D transferring booster pump | P-32C | K3 / 3R3 | CG | 12.5/9.3 | 03.04.0912.12.13 |  |  | 03.04.09 |  |  |  | 12.12.13 |  |  |  |  | 2
489 | E-12 thermic fluid circulation pump | P-33A | K3/ 2F3 | ABB | 12.5/9.3 | 09.11.09 |  |  | 09.11.09 | [5 empty] | 09.02.15 |  |  | 2
490 | E-12 thermic fluid circulation pump | P-33B | K3 / 2F4 | ABB | 12.5/9.3 | 09.11.09 |  |  | 09.11.09 | [8 empty] | 1
491 | D-20 DM water V-303 | P-34A | K3 / 3F2 | ABB | 10/7.5 | 07.06.11 |  |  |  |  | 07.06.11 |  |  |  | 05.09.2015 |  | 28.02.17 | 3
492 | D-20 DM water V-303 | P-34B | K3 / 3F3 | ABB | 10/7.5 | 09.11.0930.07.14 |  |  | 09.11.09 |  |  |  |  | 30.07.14 |  |  |  | 2
493 | Hotwell Pump | P-360A | UMCC/3F2 | Siemens | 30 | installed 1230.08.1326.01.14/29.12.14 | [5 empty] | installed 12 | 30.08.13 | 26.01.14/29.12.14 |  |  |  | 3
494 | Hotwell Pump | P-360B | UMCC/2F2 | Siemens | 30 | installed 1221.10.1302.04.14 | [5 empty] | installed 12 | 21.10.13 | 02.04.14 |  | 25.10.16 |  | 4
495 | Cooling water pump-K3' | P-362A | UMCC/3F3 | Siemens | 90 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
496 | Cooling water pump-K3' | P-362B | UMCC/5F3 | Siemens | 90 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
497 | Cooling water pump-Jutasama | P-362C | UMCC/5F2 | Siemens | 45 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
498 | Cooling water pump-Jutasama | P-362D | UMCC/2F3 | Siemens | 75 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
499 | DM water pump | P-363A | UMCC/3R2 | ABB | 11 | installed 12 | [5 empty] | installed 12 |  |  |  | 23.11.16 |  | 2
500 | DM water pump | P-363B | UMCC/3R3 | Siemens | 11 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
501 | Clean CW Pump -Precon & Postcon | P-364A | UMCC/4F3 | Siemens | 75 | installed 12 | [5 empty] | installed 12 |  |  |  | 12.11.16 |  | 2
502 | Clean CW Pump -Precon & Postcon | P-364B | UMCC/3R4 | Siemens | 75 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
503 | Dirty Water Pump | P-365A | UMCC/2F1 | Siemens | 2.2 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
504 | Dirty Water Pump | P-365B | UMCC/3F1 | Siemens | 2.2 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
505 | K-3 Reboiler thermic fluid circulation pump | P-36A | K3 / 2F1 | CG | 30/22 | 29.04.11/10.11.1125.03.14 |  |  |  |  | 29.04.11/10.11.11 |  |  | 25.03.14 | 04.05.15 | 05.11.16 |  | 4
506 | K-3 Reboiler thermic fluid circulation pump | P-36B | K3 / 3F1 | CG | 30/22 | 09.11.0902.04.12 |  |  | 09.11.09 |  |  | 02.04.12 |  |  | 08.02.15 |  |  | 3
507 | Feed pump to D-10 | P-3A | K3 / 3R1 | CG | 5/3.7 | 18.11.09 |  |  | 18.11.09 | [5 empty] | 20.11.2015 |  |  | 2
508 | Feed pump to D-10 | P-3B | K3 / 3R1 | CG | 5/3.7 | 16.02.10/01.04.1003.09.1218.04.14 |  |  |  | 16.02.10/01.04.10 |  | 03.09.12 |  | 18.04.14 |  |  | 01.03.17 | 4
509 | LE transfer pump-1 | P-402A | 103/9F1 | Siemens | 3/2.2 | [12 empty] | 0
510 | LE transfer pump-2 | P-402B | 103/9F2 | Siemens | 3/2.2 | [12 empty] | 0
511 | Residue transfer pump-1 | P-407A | 103/1F3 | Siemens | 12.5/9.3 | 13.05.14 | [7 empty] | 13.05.14 |  |  |  | 1
512 | Residue transfer pump-2 | P-407B | 103/1F4 | Siemens | 12.5/9.3 | [12 empty] | 0
513 | Dryer circulation pump-1 | P-408A | 103/2F1 | Siemens | 20/15 | [12 empty] | 0
514 | Dryer circulation pump-2 | P-408B | 103/2F2 | Siemens | 20/15 | [12 empty] | 0
515 | LE transfer pump fromV-403-1 | P-409A | 103/10F1 | Siemens | 3/2.2 | 23.08.13 | [6 empty] | 23.08.13 |  |  |  |  | 1
516 | LE transfer pump fromV-403-2 | P-409B | 103/10F2 | Siemens | 3/2.2 | [12 empty] | 0
517 | Bottom circulation pump for C-402-1 | P-410A | 103/2F3 | Siemens | 20/15 | [12 empty] | 0
518 | Bottom circulation pump for C-402-2 | P-410B | 103/2F4 | Siemens | 20/15 | [12 empty] | 0
519 | Hot oil transfer pump for ER-402-1 | P-411A |  |  | 18.5kw | 10.11.12 | [5 empty] | 10.11.12 | [5 empty] | 1
520 | Hot oil transfer pump for ER-402-2 | P-411B | 103/5F4 | Siemens | 25/18.5 | [12 empty] | 0
521 | Distillate transfer pump-1 | P-412A | 103/6F1 | Siemens | 25/18.5 | [12 empty] | 0
522 | Distillate transfer pump-2 | P-412B | 103/6F2 | Siemens | 25/18.5 | [9 empty] | 07.07.15 |  |  | 1
523 | HFA transfer pump-1 | P-414A | 103/9F3 | Siemens | 5/3.7 | [12 empty] | 0
524 | HFA transfer pump-2 | P-414B | 103/9F4 | Siemens | 5/3.7 | [12 empty] | 0
525 | Hot oil booster pump-1 | P-418A | 103/3F1 | Siemens | 12.5/9.3 | [12 empty] | 0
526 | Hot oil booster pump-2 | P-418B | 103/3F2 | Siemens | 12.5/9.3 | [12 empty] | 0
527 | SFA feed pump-1 | P-419A | 103/1F5 | Siemens | 12.5/9.3 | [12 empty] | 0
528 | SFA feed pump-2 | P-419B | 103/1F3 | Siemens | 12.5/9.3 | [12 empty] | 0
529 | Hot oil transfer pump -1 | P-420A | 103/3F4 | Siemens | 2/1.5 | 18.11.0917.02.11 |  |  | 18.11.09 |  | 17.02.11 | [6 empty] | 2
530 | Hot oil transfer pump -2 | P-420B | 103/4F1 | Siemens | 2/1.5 | [12 empty] | 0
531 | L/E transfer pump | P-421A | D2/7F2 | Bharat Bijlee | 7.5/5.5 | 10.09.2014 | [7 empty] | 10.09.2014 |  |  |  | 1
532 | L/E transfer pump | P-421B | D2/7F1 | Bharat Bijlee | 7.5/5.5 | 05.12.0908.11.1011.12.1320.10.14 |  |  | 05.12.09 | 08.11.10 |  |  | 11.12.13 | 20.10.14 |  |  |  | 4
533 | Direct cooling water return pump-1 | P-422A | 103/8F1 | Siemens | 30/22 | 23.02.11 |  |  |  |  | 23.02.11 | [6 empty] | 1
534 | Direct cooling water return pump-2 | P-422B | 103/8F2 | Siemens | 30/22 | 05.01.0918.12.14 |  |  | 05.01.09 |  |  |  |  | 18.12.14 | 14.10.2015 |  |  | 3
535 | Direct cooling water return pump | P-422C | M103/8F1 | Bharat Bijlee | 50/37 | 18.09.14 | [7 empty] | 18.09.14 |  |  |  | 1
536 | Direct cooling water return pump | P-422D | M103/8F2 | Bharat Bijlee | 50/37 | [12 empty] | 0
537 | C401 Reboiler circulation pump | P-423A |  |  | 30kw | 19.02.08 |  | 19.02.08 | [9 empty] | 1
538 | C401 Reboiler circulation pump | P-423C |  |  | 30KW | 11.07.13 | [6 empty] | 11.07.13 |  |  |  |  | 1
539 | Column 401 reboiler circulation pump | P-423D |  |  | 30kw | 28.02.13 | [6 empty] | 28.02.13 |  |  |  |  | 1
540 | Internal Circulation Pump | P-426A | D2/5F3 | SIEMENS | 25/18.5 | [12 empty] | 0
541 | Internal Circulation Pump | P-426B | D2/5F4 | Bharat Bijlee | 15/11 | [12 empty] | 0
542 | ICW circulation pump-1 | P-430A | 112/2F2 | Siemens | 15/11 | [12 empty] | 0
543 | ICW circulation pump-2 | P-430B | 112/2F3 | Siemens | 15/11 | [12 empty] | 0
544 | ICW circulation pump-3 | P-430C | 112/3F2 | Siemens | 15/11 | [12 empty] | 0
545 | Dryer Circulation Pump | P-431A | D2/8R1 | Bharat Bijlee | 25/18.5 | 04.02.13/23.02.13 | [6 empty] | 04.02.13/23.02.13 |  | 19.11.15 | 08.12.16 |  | 3
546 | Dryer Circulation Pump | P-431B | D2/R2 | Bharat Bijlee | 25/18.5 | 17.05.12/23.09.12 | [5 empty] | 17.05.12/23.09.12 | [5 empty] | 1
547 | New SPD feed | P-450A |  |  | 9.3 | [12 empty] | 0
548 | New SPD feed | P-450B |  |  | 9.3 | [12 empty] | 0
549 | Motor For Dehydrator Pump P-451A | P-451A |  |  | 11 | [12 empty] | 0
550 | Motor For Dehydrator Pump P-451B | P-451B |  |  | 11 | 22.02.14/25.12.14 | [7 empty] | 22.02.14/25.12.14 |  |  |  | 1
551 | Motor For Steam Separator P-452A | P-452A |  |  | 18.5 | [12 empty] | 0
552 | Motor For Steam Separator P-452B | P-452B |  |  | 18.5 | [12 empty] | 0
553 | Motor For Thermic Fluid Circulation preheater P-453A | P-453A |  |  | 5.5 | [12 empty] | 0
554 | Motor For Thermic Fluid Circulation preheater P-453B | P-453B |  |  | 5.5 | [12 empty] | 0
555 | Motor For SPD main distillate P-454A | P-454A |  |  | 5.5 | [12 empty] | 0
556 | Motor For SPD main distillate P-454B | P-454B |  |  | 5.5 | [12 empty] | 0
557 | Motor For SPD Bottom P-455A | P-455A |  |  | 7.5 | [12 empty] | 0
558 | Motor For SPD Bottom P-455B | P-455B |  |  | 7.5 | [12 empty] | 0
559 | HOT WELL CIRCULATION-1 | P-456A |  |  | 30 | [12 empty] | 0
560 | Motor For Hot well Circulation P-456A | P-456B |  |  | 30 | 18.04.14 | [7 empty] | 18.04.14 | 09.05.15 |  |  | 2
561 | Motor For Thermic Fluid water Circulation Reboiler P-457A | P-457A |  |  | 11 | [12 empty] | 0
562 | THERMIC FLUID WATER CIRCULATION REBOILER-2 | P-457B |  |  | 11 | [12 empty] | 0
563 | D-10 to K-3 | P-4A | 1R3 | SIE | 30/22 | 06.02.1122.12.13 |  |  |  |  | 06.02.11 |  | 22.12.13 |  |  | 22.09.16 |  | 3
564 | D-10 to K-3 | P-4B | K3/ 3R4 | CG | 20/15 | 12.07.12/24.12.1215.01.14 | [5 empty] | 12.07.12/24.12.12 |  | 15.01.14 |  |  |  | 2
565 | Bottom circulation pump | P-511A | k4 / 2R5 | BBL | 15 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
566 | Bottom circulation pump | P-511B | k4 / 2R6 | BBL | 15 | installed in 1105.06.14 |  |  |  |  | installed in 11 |  |  | 05.06.14 |  |  |  | 2
567 | Bottom draw pump | P-512A | K4 / 2F4 | SIEMENS | 3.7 | 01.08.1009.05.11/22.01.11 |  |  |  | 01.08.10 | 09.05.11/22.01.11 | [6 empty] | 2
568 | Bottom draw pump | P-512B | K4 / 2F5 | BBL | 3.7 | 25.03.1109.03.14 |  |  |  |  | 25.03.11 |  |  | 09.03.14 |  |  |  | 2
569 | Hot oil circulation pump | P-513A | K4 / 3F3 | BBL | 30 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
570 | Hot oil circulation pump | P-513B | K4/ 5F3 | BBL | 30 | installed in 11 |  |  |  |  | installed in 11 |  |  |  |  | 22.06.2016 |  | 2
571 | Distillate transfer pump | P-514A | K4 / 4F3 | SIEMENS | 9.3 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
572 | Distillate transfer pump | P-514B | K4 / 4F4 | BBL | 7.5 | installed in 1107.05.14 |  |  |  |  | installed in 11 |  |  | 07.05.14 |  |  |  | 2
573 | Pump for steam generator | P-515A | K4 /5F2 | BBL | 18.5 | installed in 1109.04.14 |  |  |  |  | installed in 11 |  |  | 09.04.14 |  |  |  | 2
574 | Pump for steam generator | P-515B | K4 / 5R4 | BBL | 18.5 | installed in 1117.01.14 |  |  |  |  | installed in 11 |  |  | 17.01.14 | june 15'/23.08.2015/Nov 2015 |  |  | 3
575 | Light end transfer pump | P-516A | K4/ 2F1 | BBL | 2.2 | 23.02.13 | [6 empty] | 23.02.13 |  | 11.06.15 | 01.08.16 |  | 3
576 | Light end transfer pump | P-516B | K4/ 2F2 | BBL | 1.5 | 30.03.13 | [6 empty] | 30.03.13 |  |  |  |  | 1
577 | SPD Distilate Transfer Pump | P-517A | k4/2F3 | NORD | 1.5 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
578 | SPD Distilate Transfer Pump | P-517B | K4/2F6 | NORD | 1.5 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
579 | SPD Distilate Residue Transfer Pump | P-518A | K4/3F2 | NORD | 1.1 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
580 | SPD Distilate Residue Transfer Pump | P-518B | K4/4F2 | NORD | 1.1 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
581 | Thermic fluid pump | P-519A | K4/4F6 | BBL | 7.5 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
582 | Thermic fluid pump | P-519B | K4/5F1 | BBL | 7.5 | installed in 1129.11.13 |  |  |  |  | installed in 11 |  | 29.11.13 |  |  |  |  | 2
583 | Feed pump for SPD | P-520 | K4/3F1 | BBL | 2.2 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
584 | Vaccum pump | P-522 | K4/4F1 | CG | 5.5 | installed in 1118.05.14 |  |  |  |  | installed in 11 |  |  | 18.05.14 |  |  |  | 2
585 | CRUDE SWEET WATER TRANSFER PUMP | P-604C | GDU MCC/5R6 | Bharat bijlee | 11 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
586 | CIP | P-630 | GDU MCC/3F5 |  | 5.5 | [12 empty] | 0
587 | Transfer/Recirculation | P-631A | GDU MCC/4F1 |  | 5.5 | [12 empty] | 0
588 | Transfer/Recirculation | P-631B | GDU MCC/4F2 |  | 5.5 | [12 empty] | 0
589 | Transfer/Recirculation | P-632A | GDU MCC/4F3 |  | 5.5 | [12 empty] | 0
590 | Transfer/Recirculation | P-632B | GDU MCC/5F2 |  | 5.5 | [12 empty] | 0
591 | Transfer/Recirculation | P-633A | GDU MCC/3R4 |  | 15 | [12 empty] | 0
592 | Transfer/Recirculation | P-633B | GDU MCC/3R5 |  | 15 | [12 empty] | 0
593 | Condensate Pump | P-634A | GDU MCC/2F3 |  | 2.2 | [12 empty] | 0
594 | Condensate Pump | P-634B | GDU MCC/2F4 |  | 2.2 | [12 empty] | 0
595 | Condensate Pump | P-635A | GDU MCC/5F5 |  | 7.5 | [12 empty] | 0
596 | Condensate Pump | P-635B | GDU MCC/5F6 |  | 7.5 | [12 empty] | 0
597 | Feed Pump | P-651 | GDU MCC/3R6 |  | 15 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
598 | Product x'per pump | P-651A | MCC121/2F3 | SIEMENS | 15 kw | 29.06.14 | [7 empty] | 29.06.14 | 10.01.15 | 12.03.16, 15.03.16 |  | 3
599 | Product x'per pump | P-651B | MCC121/3F2 | SIEMENS | 3.7 kw | 27.03.11 |  |  |  |  | 27.03.11 | [6 empty] | 1
600 | Transfer/Recirculation | P-652 | GDU MCC/3R1 |  | 15 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
601 | Hot water x'per pump-1 | P-652A | MCC121/4F2 | PRIMO | 3.7 kw | 19.12.0721.02.1021.11.13 | 19.12.07 |  |  | 21.02.10 |  |  | 21.11.13 |  |  |  |  | 3
602 | Hot water x'per pump-2 | P-652B | MCC121/2R1 | Bharat bijlee | 3.7 kw | 22.07.1111.05.12 |  |  |  |  | 22.07.11 | 11.05.12 | [5 empty] | 2
603 | Transfer/Recirculation | P-653 | GDU MCC/3R2 |  | 15 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
604 | C.W.R.Pump(Pastillator Ground Floor) | P-653B | MCC121/4R4 | No Name Plate | 9.3 | 31.10.07 | 31.10.07 | [10 empty] | 1
605 | Transfer/Recirculation | P-654 | GDU MCC/4R2 |  | 15 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
606 | Product Pump | P-655 | GDU MCC/4R3 |  | 15 | installed in 1206.02.13 | [5 empty] | installed in 12 | 06.02.13 |  | 19.11.2015 |  |  | 3
607 | Condensate Pump | P-656A | GDU MCC/2F5 |  | 2.2 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
608 | Condensate Pump | P-656B | GDU MCC/3F1 |  | 2.2 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
609 | Condensate Pump | P-657A | GDU MCC/2R5 |  | 5.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
610 | Condensate Pump | P-657B | GDU MCC/2R6 |  | 5.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
611 | Hot Oil Pump | P-685 | GDU MCC/3F4 | ABB | 3.7 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
612 | Crude Glycerin Transfer pump | P-686 | GDU MCC/5R5 | ABB | 15 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
613 | Hot Well pump | P-687 | GDU MCC/2F2 | Bharat bijlee | 22 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
614 | Sweet water hot well pump | P-688 | GDU MCC/3F2 | Bharat bijlee | 2.2 | installed in 1214.09.14 | [5 empty] | installed in 12 |  | 14.09.14 |  |  |  | 2
615 | Precon Sweet water pump | P-689 | GDU MCC/4R1 |  | 7.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
616 | vessel 702 bottom circulation pump | P-702 A | D2/2F1 |  | 7.5/5.5 | 14.04.11 |  |  |  |  | 14.04.11 | [6 empty] | 1
617 | vessel 702 bottom circulation pump | P-702B | M111 |  | 7.5/5.5 | [12 empty] | 0
618 | Finish Material Tr. Pump | P-704A | D2 /2F4 | Crompton greaves | 7.5/5.5 | [12 empty] | 0
619 | Finish Material Tr. Pump | P-704B | D2 /2F5 | Crompton greaves | 7.5/5.5 | [12 empty] | 0
620 | Circulation Pump | P-705 | 111/5R3 | Crompton greaves | 75/55 | [12 empty] | 0
621 | D.M. Water Pump | P-706A |  | Bharat Bijlee | 5/3.7 | [12 empty] | 0
622 | D.M. Water Pump | P-706B | 111/5F2 | Crompton greaves | 5/3.7 | 29.06.0917.08.1124.06.13 |  |  | 29.06.09 |  | 17.08.11 |  | 24.06.13 |  |  |  |  | 3
623 | TANK FORM FEED PUMP | P-7100A |  |  | 9.3 | installed in 1318.02.14/13.08.14 | [6 empty] | installed in 13 | 18.02.14/13.08.14 |  |  |  | 2
624 | TANK FORM FEED PUMP | P-7100B |  |  | 3.7 | installed in 1318.02.14 | [6 empty] | installed in 13 | 18.02.14 |  |  |  | 2
625 | CRUDE RECIRCULATION PUMP | P-7101 |  |  | 11 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
626 | DEODERIZER DRYER RECIRCULATION PUMP | P-7102 |  |  | 2.2 | 20.03.1312.05.14 | [6 empty] | 20.03.13 | 12.05.14 |  | 20.08.16 |  | 3
627 | FEED PUMP | P-7103 |  |  | 2.2 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
628 | RESIDUE TRANSFER PUMP | P-7104A |  |  | 3.7 | installed in 1318.04.14 | [6 empty] | installed in 13 | 18.04.14 |  |  |  | 2
629 | RESIDUE TRANSFER PUMP | P-7104B |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  |  |  | 01.03.17 | 2
630 | DISTILLATE PUMP | P-7106 |  |  | 5.5 | 15.06.13 | [6 empty] | 15.06.13 |  | 14.01.15 |  |  | 2
631 | BLEACHER FEED PUMP | P-7107 |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
632 | SUB STANDARD GLYCERINE TRANSFER PUMP | P-7108 |  |  | 2.2 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
633 | Vaccum Pump | P-710A | 111/5F5 | Crompton greaves | 7.5/5.5 | 12.09.09installed in 13 |  |  | 12.09.09 |  |  |  | installed in 13 |  |  |  |  | 2
634 | Vaccum Pump | P-710B | 111/5F6 | Crompton greaves | 7.5/5.5 | 24.03.1123.02.13 |  |  |  |  | 24.03.11 |  | 23.02.13 |  | 12.09.2015 |  |  | 3
635 | Hot Well Pump | P-711 | 111/5R1 | Crompton greaves | 20/15 | [12 empty] | 0
636 | PITCH PUMP | P-7110B |  |  | 3.7 | installed in 1314.07.14 | [6 empty] | installed in 13 | 14.07.14 |  |  |  | 2
637 | INTERMEDIATE DISTILLED GLYCERINE X-MER PUMP | P-7111 |  |  | 2.2 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
638 | FLASH VESSEL-II | P-7112 |  |  | 2.2 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
639 | X-FER PUMP FROM ATFD RECEIVER | P-7113 |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
640 | X-FER PUMP FROM HOT WELL TO COOLING WATER | P-7114A |  |  | 37 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
641 | X-FER PUMP FROM HOT WELL TO COOLING WATER | P-7114B |  |  | 18.5 | 01.06.1303.08.14 | [6 empty] | 01.06.13 | 03.08.14 |  |  |  | 2
642 | COOLING TOWER X-FER PUMP-1 | P-7115A |  |  | 18.5 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
643 | COOLING TOWER X-FER PUMP-2 | P-7115B |  |  | 5.5 | installed in 1312.03.14/05.09.2014/13.09.14 | [6 empty] | installed in 13 | 12.03.14/05.09.2014/13.09.14 |  |  |  | 2
644 | INTERMEDIATE REFINED GLYCERINE X-FER PUMP | P-7117 |  |  | 5.5 | 19.09.13 | [6 empty] | 19.09.13 |  | 15.10.2015 |  |  | 2
645 | FIRST STAGE FLASH PUMP | P-7118 |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
646 | SECOND STAGE FLASH PUMP | P-7119 |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
647 | ATFD FEED PUMP | P-7120 |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  | 25.02.15 | 19.12.16 |  | 3
648 | SCRUBBER CIRCULATION PUMP | P-7121 |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
649 | HOT OIL X-FER PUMP FOR E-101 | P-7122 |  |  | 7.5 | installed in 1302.03.14/0811.14 | [6 empty] | installed in 13 | 02.03.14/0811.14 | 07.05.15 |  |  | 3
650 | HOT OIL X-FER PUMP FOR E-102 | P-7123 |  |  | 2.2 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
651 | HOT OIL FOR ATFD | P-7124 |  |  | 2.2 | 17.02.13 | [6 empty] | 17.02.13 |  |  |  |  | 1
652 | SCRUBBER DISCHARGE PUMP | P-7125 |  |  | 15 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
653 | SCRUBBER CIRCULATION PUMP | P-7126A |  |  | 3.7 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
654 | SCRUBBER CIRCULATION PUMP | P-7126B |  |  | 9.3 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
655 | SCRUBBER CIRCULATION PUMP | P-7126C |  |  | 9.3 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
656 | SCRUBBER CIRCULATION PUMP | P-7126D |  |  | 11 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
657 | FINISHED GOOD LOADING PUMP | P-7127 |  |  | 9.3 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
658 | PIT PUMP | P-7128 |  |  | 2.2 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
659 | Trolly Unloading Pump-1 | P-801A | 105/3R4 | Siemens | 60/45 | [11 empty] | 12.01.17 | 1
660 | Trolly Unloading Pump-1 | P-801A | D2/2F2 | Bharat Bijlee | 7.5/5.5 | [12 empty] | 0
661 | Trolly Unloading Pump-2 | P-801B | 105/2R4 | Siemens | 60/45 | [12 empty] | 0
662 | Trolly Unloading Pump-2 | P-801B | D2/3F2 | Bharat Bijlee | 7.5/5.5 | [12 empty] | 0
663 | TROLLY UNLOADING PUMP-4 | P-801D |  |  | 45kw | 17.02.1201.03.14 | [5 empty] | 17.02.12 |  | 01.03.14 |  |  |  | 2
664 | Crude oil transfer pump-1 | P-802A | 105/4F4 | Siemens | 18.5 | 09.12.0827.07.1123.06.14 |  | 09.12.08 |  |  | 27.07.11 |  |  | 23.06.14 |  | 22.02.2016 & 11.12.16 |  | 4
665 | Crude oil transfer pump-2 | P-802B | 105/2F4 | Siemens | 15 | 14.12.08 |  | 14.12.08 | [7 empty] | 17.03.16 |  | 2
666 | Crude oil transfer pump-3 | P-802C |  | Siemens | 18.5 | [10 empty] | 25.06.2016 & 12.12.16 | 05.02.17 | 2
667 | FEED PUMP | P-803 | D2/3F3 |  | 7.5/5.5 | [12 empty] | 0
668 | Feed for C-301/302 | P-804A | 105/3F2 | Siemens | 7.5/5.5 | [12 empty] | 0
669 | Feed for C-301/302 | P-804B | 105/4R3 | Siemens | 7.5/5.5 | [12 empty] | 0
670 | C12 LAURIC/PKD unloading pump-1 | P-806A | 105/2F4 | Siemens | 30/22 | [12 empty] | 0
671 | C12 LAURIC/PKD unloading pump-2 | P-806B | 105/4F5 | Siemens | 30/22 | [12 empty] | 0
672 | C12 LAURIC/PKD transfer pump-1 | P-807A | 105/2F3 | Siemens | 10/7.5 | [12 empty] | 0
673 | C12 LAURIC/PKD transfer pump-2 | P-807B | 105/5F3 | Siemens | 10/7.5 | [12 empty] | 0
674 | k3 feed pump | P-808 | 105/5F5 | Siemens | 20/15 | [12 empty] | 0
675 | Old K3/k4 feed | P-808B |  |  | 11kw | 27.10.12 | [5 empty] | 27.10.12 | [5 empty] | 1
676 | Feed alcohol | P-809 | 105/5F6 | Siemens | 20/15 | 06.02.09 |  |  | 06.02.09 | [8 empty] | 1
677 | C16/18 Transfer pump | P-810 | 105/4R4 | Siemens | 5.5/7.5 | [12 empty] | 0
678 | 401/402 Feed pump | P-811A | 105/3R2 | Siemens | 7.5/5.5 | [12 empty] | 0
679 | 401/402 Feed pump | P-811B | 105/2R2 | Siemens | 7.5/5.5 | [12 empty] | 0
680 | Distilled FPAD/CPS transfer pump | P-812A | 105/3F3 | Siemens | 12.5/9.3 | [12 empty] | 0
681 | Heavy end transfer pump-1 | P-813A | 105/3R3 | Siemens | 10/7.5 | [12 empty] | 0
682 | Heavy end transfer pump-2 | P-813B | 105/4R5 | Siemens | 10/7.5 | [12 empty] | 0
683 | PFAD/CPS transfer pump | P-814 | 105/2R3 | Siemens | 7.5/5.5 | [12 empty] | 0
684 | Glycepine transfer pump | P-815 | 105/1R3 | Siemens | 7.5/5.5 | [12 empty] | 0
685 | Condensate transfer pump-1 | P-816A | [13 empty] | 29.09.16 |  | 1
686 | Condensate transfer pump-2 | P-816B | 105/1R2 | Siemens | 1.5/1.1 | 14.06..14 | [7 empty] | 14.06..14 |  |  |  | 1
687 | Loading Unloading pump | P-817 | TF4-6F3 | ABB | 11 | [12 empty] | 0
688 | ISO LOADING PUMP | P-818 | TF4-3F1 | ABB | 7.5 | [12 empty] | 0
689 | Loading Unloading pump | P-819A | TF4-4F4 | ABB | 5.5 | [9 empty] | 23.07.15 |  |  | 1
690 | Loading Unloading pump | P-819B | TF4-4F4 | ABB | 5.5 | [9 empty] | 14.07.15 |  |  | 1
691 | Loading Unloading pump | P-820 | TF4-5F2 | ABB | 11 | [12 empty] | 0
692 | Loading Unloading pump | P-821 | TF4-3F2 | ABB | 7.5 | [12 empty] | 0
693 | Loading Unloading pump | P-822 | TF4-4F3 | ABB | 5.5 | [12 empty] | 0
694 | Oil dhakka circulation pump | P-823 |  |  | 45kw | 25.10.12 | [5 empty] | 25.10.12 | [5 empty] | 1
695 | Oil dhakka circulation pump | P-824 |  |  | 3.7kw | 28.11.1221.1014 | [5 empty] | 28.11.12 |  | 21.1014 |  |  |  | 2
696 | CW supply Pump for Splitting & SW | P-9002A | Precon MCC/1F1 | BBL | 90 | installed in 1206.05.14 | [5 empty] | installed in 12 |  | 06.05.14 |  |  |  | 2
697 | CW supply Pump for Splitting & SW | P-9002B | Precon MCC/2F1 | schorch | 80 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
698 | Tempered water pump | P-901A | K4/5R2 | BBL | 11 | 22.07.11 |  |  |  |  | 22.07.11 | [6 empty] | 1
699 | Tempered water pump | P-901B | K4/3R3 | BBL | 22 | [12 empty] | 0
700 | Indirect cooling water pump-1 | P-903A | 112/2F4 | Siemens | 100/75 | [12 empty] | 0
701 | Indirect cooling water pump-2 | P-903B | 112/3F3 | Siemens | 100/75 | [12 empty] | 0
702 | Indirect cooling water pump-3 | P-903C | 112/4F4 | Siemens | 100/75 | [12 empty] | 0
703 | Indirect cooling water pump-4 | P-903D | 112/3R3 | Siemens | 100/75 | [12 empty] | 0
704 | Fo transfer pump | P-905A | 113/3F1 | Cromption greaves | 3/2.2 | [12 empty] | 0
705 | Fo transfer pump | P-905B | 113/3F2 | Cromption greaves | 3/2.2 | [12 empty] | 0
706 | RW transfer pump | P-906-A | 113/2F2 | Siemens | 20/15 | [12 empty] | 0
707 | RW transfer pump | P-906-B | 113/2F3 | Siemens | 20/15 | [12 empty] | 0
708 | RW transfer pump | P-906-C | 113/3F3 | Siemens | 20/15 | [12 empty] | 0
709 | D.M.Water transfer pump | P-908 | 111/2F3 | Siemens | 7.5/5.5 | 23.05.08 |  | 23.05.08 | [9 empty] | 1
710 | Intermediate pump for mp boiler | P-909 | 113/3R4 | Siemens | 10/7.5 | [12 empty] | 0
711 | Cooling water return pump | P-910A | K4/4F5 | BBL | 7.5 | 18.07.11/17.11.1130.11.12 |  |  |  |  | 18.07.11/17.11.11 | 30.11.12 | [5 empty] | 2
712 | Cooling water return pump | P-910B | K4/5R1 | BBL | 7.5 | installed in 11 |  |  |  |  | installed in 11 |  |  |  |  | 22.05.2016 |  | 2
713 | WTP Pump-1 | P-913 | 113/3R2 | Siemens | 5/3.7 | [12 empty] | 0
714 | Filtered water booster pump | P-914 | 113/3R1 | Siemens | 15/11 | [12 empty] | 0
715 | D.M.Water transfer pump-1 | P-919A | 111/2R2 | Siemens | 12.5/9.3 | 30.11.09 |  |  | 30.11.09 | [8 empty] | 1
716 | D.M.Water transfer pump-2 | P-919B | 111/2R3 | Siemens | 12.5/9.3 | [12 empty] | 0
717 | Blowdown transfer pump | P-920 | 111/3R5 | Siemens | 3/2.2 | 21.12.08 |  | 21.12.08 | [9 empty] | 1
718 | Chilling water transfer pump-1 | P-951A | MCC121/3F1 | Kirloskar | 50/37 | [12 empty] | 0
719 | Chilling water transfer pump-2 | P-952A | MCC121/4F3 | Kirloskar | 20/15 | [12 empty] | 0
720 | Chilled water secondry Pump | P-953A | MCC121/2R2 | Bharat bijlee | 5/3.7 | [12 empty] | 0
721 | CHW secondary stnd by pump for P953A | P-953B | MCC121/2R3 | Bharat bijlee | 15/11 | [12 empty] | 0
722 | Chiller compressor | P-954A | FLKMCC/3F1 | SIEMENS | 150/110 | 30.01.12 | [5 empty] | 30.01.12 | [5 empty] | 1
723 | Chilling water pump | P-955 |  |  | 11kw | 30.11.08 |  | 30.11.08 | [9 empty] | 1
724 | Clean condensate Pump | P-CD100 | UMCC/5F1 | Siemens | 2.2 | [12 empty] | 0
725 | Reactor Agitator | R101 | PILOT MCC/2F2 | CG | 3.7/5 | installed in 10 |  |  |  | installed in 10 | [7 empty] | 1
726 | Bleacher Agitator | R102 | PILOT MCC/2F3 | CG | 3.7/5 | 04.07.10 |  |  |  | 04.07.10 | [7 empty] | 1
727 | belt conveyor | rav1 |  |  | 0.37kw | 17.11.09 |  |  | 17.11.09 | [8 empty] | 1
728 | Stirrer for SPD | S-509 | K4/3R1 | BBL | 11 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
729 | Agitator motor | Tank-803 |  |  | 3.7kw | 20.02.13 | [6 empty] | 20.02.13 |  |  |  |  | 1
730 | D2 MCC 7F4 | TF - 22 | D2/7F3 | [14 empty] | 0
731 | Feed for C-401/402 | TF-12A | D2/7F5 | Bharat bijlee | 7.5/5.7 | [12 empty] | 0
732 | Feed for C-401/402 | TF-12B | TF4 MCC/2F2 | ABB | 7.5/5.7 | [12 empty] | 0
733 | LOOP FEED PUMP | TF-33A | D2/8R5 | C.G. | 7.5/5.5 | [12 empty] | 0
734 | Feed for C-301/303 | TF-33B | TF4 MCC/2F1 |  | 7.5/5.5 | [12 empty] | 0
735 | UNLOAD PUMP TK1 | TF4-11 | TF4 MCC/6F1 | Bharat bijlee | 25/18.5 | [12 empty] | 0
736 | FEED TO LR | TF4-21 | TF4 MCC/6F2 | Bharat bijlee | 25/18.5 | [12 empty] | 0
737 | UNLOAD PUMP TK3 | TF4-31 | D2 /5R4 |  |  | 20.05.10 |  |  |  | 20.05.10 | [7 empty] | 1
738 | FEED TO FLAKER-1 | TF4-32A | TF4 MCC/5F3 | Bharat bijlee | 5/3.7 | [12 empty] | 0
739 | FEED TO FLAKER-2 | TF4-32B | TF4 MCC/5F4 | Bharat bijlee | 5/3.7 | 28.08.09 |  |  | 28.08.09 | [5 empty] | 03.03.15 |  |  | 2
740 |  | TF4-32C | [12 empty] | 10.07.15/20.11.2015 |  |  | 1
741 | Charger Agitator | V101 | PILOT MCC/1F6 | CG | 2.2/3 | installed in 10 |  |  |  | installed in 10 | [7 empty] | 1
742 | Vacuum Pump | VP-631A | GDU MCC/5R1 |  | 15 | [12 empty] | 0
743 | Vacuum Pump | VP-631B | GDU MCC/5R2 |  | 15 | [12 empty] | 0
744 | Vacuum Pump | VP-651A | GDU MCC/5R3 |  | 15 | 17.02.09 |  |  | 17.02.09 | [8 empty] | 1
745 | Vacuum Pump | VP-651B | GDU MCC/5R4 |  | 15 | [10 empty] | 20.01.2016 |  | 1
746 | VACCUM PUMP-1 | VP-7103A |  |  | 5.5 | [12 empty] | 0
747 | VACCUM PUMP-2 | VP-7103B |  |  | 5.5 | [12 empty] | 0
748 | Water ring vacuum pump | VP-X-601A | Precon MCC/4F1 |  | 5.5 | installed in 12 | [5 empty] | installed in 12 |  |  | 03.06.15 |  |  | 2
749 | Water ring vacuum pump | VP-X-601b | Precon MCC/4F6 | ABB | 11 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
750 | Vacuum pump | VP-X-689 | GDU MCC/5F3 | ABB | 5.5 | installed in 12 | [5 empty] | installed in 12 | [5 empty] | 1
751 | VacuumPump | X - 201 | Splitting MCC/2F2 | kirloskar | 7.5 | installed in 11 |  |  |  |  | installed in 11 |  |  |  | 24.03.15 |  |  | 2
752 | vacuum Pumps (Water Ring) | X-101A | JSMCC/2R2 | Siemens | 15 | installed in 11 |  |  |  |  | installed in 11 | [6 empty] | 1
753 | vacuum Pumps (Water Ring) | X-101B | JSMCC/2R2 | Siemens | 15 | installed in 13 | [6 empty] | installed in 13 |  |  |  |  | 1
754 | Vaccum pump | X-301-1 | 103/3R2 | Siemens | 15/11 | [12 empty] | 0
755 | Vaccum pump-1 | X-401-1 | 103/4F4 | Siemens | 15/11 | 16.06.07 | 16.06.07 | [10 empty] | 1
756 | Vaccum pump-2 | X-401-2 | 103/5F5 | Siemens | 15/11 | [12 empty] | 0
757 | Blower |  | UMCC/BUS-A/2F2 | SIEMENS | 5/3.7 | [12 empty] | 0
758 | Bruckhardt Compressor-1 |  | UMCC/BUS-A/4R1 | Bharat Bijiee | 120/90 | [12 empty] | 0
759 | Bruckhardt Compressor-2 |  | UMCC/BUS-A | schorch | 80 | [12 empty] | 0
760 | Hydralic motor |  | M01/BUS-A/10F2 | Kirloskar | 3/2.2 | [12 empty] | 0
761 | Lifting belt conveyor |  | M01/BUS-B/22F5 | Kirloskar | 1/.75 | [12 empty] | 0
762 | Blower |  | M01/BUS-A/8R1 | Crompton Greaves | 5/3.7 | [12 empty] | 0
763 | Hydralic motor |  | M01/BUS-A/9F4 | SIEMENS | 3/2.2 | [12 empty] | 0
764 | Filter Press Moter A |  | M01/BUS-C/34F6 | Crompton Greaves | 2/105 | [12 empty] | 0
765 | Hydralic motor |  | M01/BUS-C/35F3 | Crompton Greaves | 3/2.2 | [12 empty] | 0
766 | HRSCC Recirculation |  | ETPMCC/4R2 | Bharat Bijiee | .75/.55 | [12 empty] | 0
767 | HRSCC Scapper |  | ETPMCC/3R3 | Bharat Bijiee | .5/.37 | [12 empty] | 0
768 | Rotadal TPI Oil Remover Pump |  | ETPMCC/5R2 | SIEMENS | 1/0.75 | [12 empty] | 0
769 | new flaker drum-2 |  | ETPMCC/ | SIEMENS | 15/11 | [12 empty] | 0
770 | Thermic Fluid F.D.Fan |  |  | Siemens | 25/18.5 | [12 empty] | 0
771 | new flaker drum-2 |  | 112/2F1 | Bharat Bijlee | 15/11 | [12 empty] | 0
772 | new flaker drum-2 |  | 112/4F2 | Bharat Bijlee | 15/11 | [12 empty] | 0
773 | back ceiling CONVER BELT NO-1 |  | NEW-FLK | Bonfiglioli Group | 0.75 | [12 empty] | 0
774 | Sewing Head Motor |  | NEW-FLK | Crompton greaves | 0.37/0.5 | [12 empty] | 0
775 | Sewing Head Motor |  | NEW-FLK | Bonfiglioli Group | 0.37/0.5 | [12 empty] | 0
776 | back ceiling CONVER BELT NO-1 |  | NEW-FLK | Bonfiglioli Group | 0.75 | [12 empty] | 0
777 | Blower |  | NEW-FLK | Crompton greaves | 3.7/5 | [12 empty] | 0
778 | new flaker drum-2 |  | 3F6 | Bharat bijlee | 15/11 | [12 empty] | 0
779 | cold well pump |  | 4f2 | Bharat bijlee | 15/12 | [12 empty] | 0
780 | Blower |  | FLKMCC/3F1 | ABB | 5/3.7 | [12 empty] | 0
781 | Blower |  | FLKMCC/2F3 | ABB | 5/3.7 | [12 empty] | 0
782 | Fridge fan blower |  | FLKMCC/2F3 | Crompton greaves | 7.5/5.5 | [12 empty] | 0
783 | PIT PUMP -1 |  |  |  | 3.7 | [12 empty] | 0
784 | chiller |  |  | SIEMENS | 45 | 24.12.07 | 24.12.07 | [10 empty] | 1
785 | Fridge fan blower |  |  | SIEMENS | 7.5/5.5 | 10.04.07 | 10.04.07 | [10 empty] | 1
786 | Fridge fan blower |  | FLKMCC/2F5 | SIEMENS | 7.5/5.5 | 13.05.07 | 13.05.07 | [10 empty] | 1
787 | new flaker blower |  |  | No Name Plate | 7.5 | 02.06.07 | 02.06.07 | [10 empty] | 1
788 | CONDENSATE TRANSFER PUMP |  |  |  | 2.2 | 02.10.12 | [5 empty] | 02.10.12 | [5 empty] | 1
789 | PIT PUMP -1 |  |  |  | 3.7 | 10.06.12 | [5 empty] | 10.06.12 | [5 empty] | 1
790 | DFA Boiler blower motor |  |  |  | 9.3kw | 10.09.07 | 10.09.07 | [10 empty] | 1
791 | TP-20 Blower |  |  |  | 5.5kw | 02.07.09 |  |  | 02.07.09 | [8 empty] | 1
792 | Vapour boiler-2 |  |  |  | 7.5kw | 26.06.09/03.08.0929.10.11 |  |  | 26.06.09/03.08.09 |  | 29.10.11 | [6 empty] | 2
793 | New IAEC boiler feed water-1 |  |  |  | 3.7kw | 26.12.07 | 26.12.07 | [7 empty] | 24.10.2015 |  |  | 2
794 | New IAEC boiler feed water-2 |  |  |  | 3.7kw | 26.12.07 | 26.12.07 | [10 empty] | 1
795 | New IAEC boiler ID fan motor |  |  |  | 18.5kw | 26.12.07 | 26.12.07 | [10 empty] | 1
796 | New IAEC boiler FD Fan motor |  |  |  | 18.5kw | 26.12.07 | 26.12.07 | [10 empty] | 1
797 | New IAEC boiler motor |  |  |  | 3.7kw | 23.04.09 |  |  | 23.04.09 | [8 empty] | 1
798 | DFA BOILER CHEMICAL DOSING PUMP |  |  |  | 0.37kw | 12.09.09 |  |  | 12.09.09 | [8 empty] | 1
799 | New IAEC boiler motor |  |  |  | 3.7kw | 22.09.09 |  |  | 22.09.09 | [8 empty] | 1
800 | ETP DAF SCRAPPER |  |  |  | 1.5kw | 14.10.09 |  |  | 14.10.09 | [8 empty] | 1
801 | Pestillator forklift hydraulic motor |  |  |  |  | 14.02.13 | [6 empty] | 14.02.13 |  |  |  |  | 1
802 | New IAEC boiler motor |  |  |  | 18.5kw | 25.03.13 | [6 empty] | 25.03.13 |  |  |  |  | 1
803 | Pestillator forklift hydraulic motor |  |  |  | 8.5kw | 09.05.13 | [6 empty] | 09.05.13 |  |  |  |  | 1
804 | VAM Purging pump |  |  |  | 0.75kw | 28.05.13/15.07.13 | [6 empty] | 28.05.13/15.07.13 |  |  |  |  | 1
805 | ETP DAF SCRAPPER |  |  |  | 1.5kw | 28.08.13 | [6 empty] | 28.08.13 |  |  |  |  | 1
806 | Storm water pump |  |  |  | 2.2KW | 22.04.13 | [6 empty] | 22.04.13 |  |  |  |  | 1
807 | Pestillator 1st floor AHU |  |  |  | 2.2KW | 28.06.13 | [6 empty] | 28.06.13 |  |  | 14.11.16 |  | 2
808 | ETP DAF SCRAPPER |  |  |  | 1.5KW | 01.10.13 | [6 empty] | 01.10.13 |  |  |  |  | 1
809 | ETP DAF SCRAPPER |  |  |  | 1.5kw | 11.12.13 | [6 empty] | 11.12.13 |  |  |  |  | 1
810 | K3 CT FAN |  |  |  | 30kw | 23.09.1231.05.13 | [5 empty] | 23.09.12 | 31.05.13 |  |  |  |  | 2
811 | Dehydrator circulation Pump | P-351A |  | Siemens | 22 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
812 |  | P-829 |  |  | 18.5kw | [8 empty] | 28.03.14 |  |  |  | 1
813 | Dehydrator circulation Pump | P-351B |  | Siemens | 22 | installed 12 | [5 empty] | installed 12 |  |  | 13.01.15 |  |  | 2
814 | Vapour boiler-1 |  |  |  | 11KW | 16.01.2014 | [7 empty] | 16.01.14 |  |  |  | 1
815 | L/E Transfer Pump of Dehydrator | P-352A |  | Siemens | 3.7 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
816 | L/E Transfer Pump of Dehydrator | P-352B |  | Siemens | 3.7 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
817 | Hot oil circulation Pump (preheater) | P-353A |  | Siemens | 22 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
818 | Hot oil circulation Pump (preheater) | P-353B |  | Siemens | 22 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
819 | Bottom recirculation pump | P-354A |  | Siemens | 75 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
820 | Bottom recirculation pump | P-354B |  | Siemens | 75 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
821 | B/P Pump K3' | P-355A |  | Siemens | 11 | installed 12 | [5 empty] | installed 12 |  |  | 12.01.15 |  |  | 2
822 | B/P Pump K3' | P-355B |  | Siemens | 11 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
823 | Hot oil circulation Pump (reboiler) | P-356A |  | Siemens | 55 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
824 | Hot oil circulation Pump (reboiler) | P-356B |  | Siemens | 55 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
825 | Pump around system pump | P-357A |  | Siemens | 37 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
826 | Pump around system pump | P-357B |  | Siemens | 37 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
827 | L/E Transfer Pump of C-303 | P-358A |  | Siemens | 5.5 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
828 | L/E Transfer Pump of C-303 | P-358B |  | Siemens | 5.5 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
829 | Side draw transfer pump of C-303 | P-359A |  | Siemens | 15 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
830 | Side draw transfer pump of C-303 | P-359B |  | Siemens | 15 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
831 | Tempered water pump | P-361A |  | Siemens | 55 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
832 | Tempered water pump | P-361B |  | Siemens | 55 | installed 12 | [5 empty] | installed 12 | [5 empty] | 1
833 | ETP Septic pump motor |  |  |  | 0.75 | 02.02.14 | [7 empty] | 02.02.14 |  |  |  | 1
834 | Peroni suction feed pump | 04G1B |  |  | 9.3 | 03.03.14 | [7 empty] | 03.03.14 |  |  |  | 1
835 | Agitator for 08T9D | 08N14D |  |  | 4 | 28.04.14 | [7 empty] | 28.04.14 |  |  |  | 1
836 |  | 01G20 |  |  | 3.7 | 01.07.14 | [7 empty] | 01.07.14 |  |  |  | 1
837 | ETP 3 Phase Submersible Pump |  |  |  |  | 01.07.14 | [7 empty] | 01.07.14 |  |  |  | 1
838 |  | P-424B |  |  | 7.5 | 05.10.14 | [7 empty] | 05.10.14 |  |  |  | 1
839 |  | 03G18A |  |  | 15 | 08.10.14 | [7 empty] | 08.10.14 | 15.07.15 |  |  | 2
840 | MCT Blicher DFA 1 floor |  |  |  | 3.7 | 07.11.14 | [7 empty] | 07.11.14 | 19.05.15 |  |  | 2
841 | coldwell pump to steel belt2 | P-962 |  |  | 18.5 | 22.11.14 | [7 empty] | 22.11.14 | 21.01.15/14.02.15/09.04.2015 |  |  | 2
842 | Agitator for 08T9A | 08N14A |  |  | 4 | 31.12.14 | [7 empty] | 31.12.14 | 09.05.15 |  |  | 2
843 | ETP Pit Pump | P-913B | [12 empty] | 09.01.15 |  | 09.03.17 | 2
844 | blower | BDG-2 | [12 empty] | 25.01.15/11.02.15 |  |  | 1
845 | Alcohol GF Filter press-A | [13 empty] | 10.02.15 |  |  | 1
846 | LOOP Reactor hot well pump | P-802B | [12 empty] | 21.03.15 |  |  | 1
847 | LOOP Reactor hot well pump | P-802A | [15 empty] | 0
848 | Mix bed blower motor (FAP Utility Boiler) | [13 empty] | 08.07.15 |  |  | 1
849 | Motor at DFA 7th Floor | P-366 | [12 empty] | 25.10.2015 |  |  | 1
850 | T-828 Agitator | [13 empty] | 30.05.2015 |  |  | 1
851 |  | 168.5 | [12 empty] | 06.09.2015 |  |  | 1
852 |  | 150.3 | [12 empty] | 04.11.2015 |  |  | 1
853 |  | 03G18B | [12 empty] | 16.11.2015 |  |  | 1
854 | Single phase motor dosa mixer | [13 empty] | 20.11.2015 |  |  | 1
855 | CGS filter press hydraulic motor | [13 empty] | 20.11.15 |  |  | 1
856 | New boiler pit pump | [13 empty] | 25.11.2015 |  |  | 1
857 |  | 05G13 | [13 empty] | 25.02.2016 |  | 1
858 |  | P-1050A2 | [13 empty] | 31.03.16 |  | 1
859 | Raw water pump-2 | 20P07B | [13 empty] | 16.04.2016 15.09.16 |  | 1
860 | Thermic fluid Pump | 1050B1 | [13 empty] | 20.06.2016 |  | 1
861 | Loop Reactor | P-705B | [13 empty] | 25.06.2016 |  | 1
862 | Coal Plant Hoist (Safex) | [14 empty] | 22.04.2016 |  | 1
863 | Agitator Motor 09U1G21A | 09U1G21A | [13 empty] | 03.03.2016/11.08.2016 |  | 1
864 | E-wax agitator motor | [14 empty] | 10.03.2016 |  | 1
865 | Cold well pump to steel belt | P-961 | [13 empty] | 05.07.16 |  | 1
866 | Beads Plant | BL-1301 | [13 empty] | 13.08.16 |  | 1
867 | Booster Pump for VAM Chilled water to GDP | [14 empty] | 24.08.16 |  | 1
868 | Flaker Chilled water recirculation pump | P-304 | [13 empty] | 24.08.16 & 08.10.16 |  | 1
869 | AUX.AIR FAN A | P-1001A | [13 empty] | 27.10.16 |  | 1
870 | AUX.AIR FAN B | P-1001B | [13 empty] | 27.10.16 |  | 1
871 | Collective Water Pump (T/F) | P-832 | [14 empty] | 31.01.17 | 1
872 | Degasser Blower | Degasser Blower |  | CG | 0.37 | [11 empty] | 19.02.17 | 1
873 | FORCED DRAFT FAN - 1 | P-1052A |  |  | 125 | [11 empty] | 05.03.17 | 1
874
875
876
877
878
879
880
881
882
883
884
885
886
887
888
889
890
891
892
893
894
895
896
897
898
899
900
901
902
903
904
905
906
907
908
909
910
911
912
913
914
915
916
917
918
919
920
921
922
923
924
925
926
927
928
929
930
931
932
933
934
Note on P54: Varun Rai: 25.06.2015 NDE side bearing Replaced in plant by fhran electric and 26.08.2015 motor send to fharan electric for total overhauling and 11.10.2015 motor burnt
Note on P136: Varun Rai: Oil cooler blower motor bearing replaced
Note on Q136: Varun Rai: Dryer Fan motor rewinding done and after some days ebm new fan installed
Note on O277: varun.rai: 03.04.2014 rotor balancing and both end cover sleeving
Note on Q277: Varun Rai: 03.03.16 DE side replaced and 4.03.16 NDE side Replaced
Note on M278: Only NDE bearing Changed
Note on N278: Due to Non-avilability of 6316C4 bearings, 6316 C3 DE & NDE both side replaced.
Note on O386: Varun Rai: Motor burnt on 16.12.14 so that spare motor given but it also burn on 18.12.14 at the time of trial.
Note on P480: Varun Rai: motor upgraded to 18.5kw. Motor changed as per new pump requirement.
Note on O538: Varun Rai: Spare motor given and old motor taken for bearing replacement
Note on P578: Varun Rai: burn twotimes in year

## Sheet2 (hidden)
TAG NO. | DESCRIPTION
125.8 | Talc system Dosing pump
128.17 | Spent lye feed pump
128.4 | Water feed pump
201.2 | Soap transfer pump
Old Flakar Drum Motor
01G10A | wax ester pump
01G10B | wax ester pump
01G11A | 01D11 Transfer Pump
01G11B | 01D11 Transfer Pump
01G12A | LIQUID RING VACCCUM PUMP
01G12B | LIQUID RING VACCCUM PUMP
01G13 | Reactor Drain out pump
01G13A | Thermic fluid pump for stripper
01G13B | Thermic fluid pump for stripper
01G14A | Tempered water pump-III
01G14B | Tempered water pump-III
01G15A | 01D10 Circulation Pump
01G15B | 01D10 Circulation Pump
01G16A | Tempered cooling water III pump
01G16B | Tempered cooling water III pump
01G17A | Scrubber Pump( FAP 3rd Floor)
01G17B | Scrubber Pump( FAP 3rd Floor)
01G18A
01G19A | Hot well to Cooling tower pump
01G19B | Hot well to Cooling tower pump
01G1A | Circulation pump for 01D1
01G1B | Circulation pump for 01D1
01G20
01G2A | Circulation pump for 01D2
01G2B | Circulation pump for 01D2
01G3A | Circulation pump for 01D3
01G3B | Circulation pump for 01D3
01G4A | Circulation pump for 01D4
01G4B | Circulation pump for 01D4
01G5A | Inline pump for 01E1
01G5B | Inline pump for 01E1
01G6A | Inline pump for 01E2
01G6B | Inline pump for 01E2
01G7A | Inline pump for 01E3
01G7B | Inline pump for 01E3
01G8A | Inline pump for 01E4
01G8B | Inline pump for 01E4
01G9A | 01E8 Thermic fluid circulation pump-1
01G9A | Inline pump for 01E8
01G9B | Inline pump for 01E8
01G9B | 01E8 Thermic fluid circulation pump-1
02G1 | H2 Compressor
02G1A | H2 Compressor
02G1AG1 | H2 Compressor main lub oil pump
02G1AG2 | H2 Compressor Aux.lub oil pump
02G1AG3 | H2 Compressor lubricator
02G1G1 | H2 Compressor main lub oil pump
02G1G2 | H2 Compressor Aux.lub oil pump
02G1G3 | H2 Compressor lubricator
02G3 | Recycle Compressor
02G3G1 | Recycle Comp. main lub oil pump
02G3G2 | Recycle Comp. Aux. lub oil pump
02G3G3 | Recycle Compressor lubricator
02G5A | HP wax ester feed pump
02G5AG1 | HP wax sealing pump motor
02G5B | HP wax ester feed pump
02G5BG1 | HP wax sealing pump motor
02G5C | HP wax ester feed pump
02G5CG1 | HP wax sealing pump motor
02G7A | Crude alcohol pump
02G7B | Crude alcohol pump
02G7C | Booster Pump
02G8A | Section-3 feed pump-1
02G8B | Section-3 feed pump-1
03G11A
03G14A | Residue recycle pump
03G14B | Residue recycle pump
03G15A | Circulation pump
03G15B | Circulation pump
03G16G3 | WR Vaccum pump
03G17A | Hot Well Pump
03G17A | Main distillated pump-1
03G17B | Hot Well Pump
03G17B | Main distillated pump-2
03G17C | Main distillated pump-3
03G1A | Circulation pump drive cycle
03G1B | Circulation pump drive cycle
03G2A | Pump for Distillate
03G2B | Pump for Distillate
03G3A | Pump for column 03D2
03G3B | Pump for column 03D2
03G4A | Inline pump for thermal oil
03G4B | Inline pump for thermal oil
03G5A | Pump for fraction from 03D2
03G5B | Pump for fraction from 03D2
03G5C | Pump for fraction from 03D2
03G6A | Inline pump for thermal oil
03G6B | Inline pump for thermal oil
03G7A | Pump for final Residue
03G7B | Pump for final Residue
03G8A | Inline pump for thermal oil
03G8B | Inline pump for thermal oil
03G9A | Inline pump for thermal oil
03G9B | Inline pump for thermal oil
04G1B
04G5A | Product pump
04G5B | Product pump
05G10A | Terpered cooling water I pump
05G10B | Terpered cooling water I pump
05G11A | Terpered cooling water II pump
05G11B | Terpered cooling water II pump
05G12A | Hot water pump-1
05G12B | Hot water pump-1
05G18A | New DM water pump-1
05G18B | New DM water pump-1
05G1A | Raw water pump
05G1B | Raw water pump
05G3A | DM water pump
05G3B | DM water pump
05G3C
05G5A | Drinking water pump
05G5B | Drinking water pump
05G7A | Fire water pump
05G8 | Jockey pump
05G9A | Cooling water pump
05G9B | Cooling water pump
05G9C | Cooling water pump
05G9D | Cooling water pump
05G9E | Cooling water pump
05G9F | Cooling water pump
05G9G | Cooling water pump
05U1G1 | Deasser blower
05U1G2 | Mixed bed blower
05U1G3 | Degassor water pump
05U1G7A | Agitator for 05U1T2A
05U1G7B | Agitator for 05U1T2B
05U1G8 | Effluent transfer pump
05U2G1A | C.T.Unit with fans
05U2G1B | C.T.Unit with fans
05U5G1 | Blower for side stream filter
06G1A | Air compressor
06G1B | Air compressor
06G1C | Air compressor
06G1D | Air compressor GA75VSD
06G1E | Air compressor GA55VSD
06G1F | Air compressor GA55
06G1G | Air compressor GA55VSD
06G2 | N2 Booster compressor
07G1A | L.P.condensate pump
07G1B | L.P.condensate pump
07G2A | FO/LSHS Unloading pump
07G3A | LDO transfer pump
07G3B | LDO transfer pump
07G4A | LDO transfer pump
07G5A | FO/LSHS Unloading pump
07G5B | FO/LSHS Unloading pump
07G7A | CONDENSATE PUMP
07G7B | CONDENSATE PUMP
07G8A | CONDENSATE PUMP
07G8B | CONDENSATE PUMP
07U1G1A | Froced draft fan bioler 5TPH
07U1G1B | Froced draft fan bioler 3TPH
07U1G2A | Bioler feed water pump 3TPH
07U1G2B | Bioler feed water pump 3TPH
07U1G3A | Bioler feed water pump 5TPH
07U1G3B | Bioler feed water pump 5TPH
07U1G5A | Fuel oil pump 5TPH
07U1G5A | Fuel oil pump 3TPH
07U1G5B | Fuel oil pump 5TPH
07U1G5B | Fuel oil pump 3TPH
07U1G7A | Ring main pump
07U1G7B | Ring main pump
07U1G8 | Agitator for doasing
07U2G1A | Thermic fluid pump
07U2G1B | Thermic fluid pump
07U2G2A | Forced draft fan
07U2G2B | Forced draft fan
07U2G5 | Sump pump
07U2G6A | Ring main pump
07U2G6B | Ring main pump
07U2G7A | LSHS/FO fuel pump
07U2G7B | LSHS/FO fuel pump
07U2G7C | LSHS/FO fuel pump
07U2G7D | LSHS/FO fuel pump
07U2G8A | LDO fuel pump
07U2G8B | LDO fuel pump
07U3G1C | Circulation pump
07U3G1D | Circulation pump
07U3G2C | FD fan
07U3G3C | Furnace oil pump
07U3G3D | Furnace oil pump
07U3G4C | ring main pump
07U3G4D | ring main pump
07U3G6C | LDO pump
08G10A | Naphtha transfer pump vertical
08G13A | Naphtha unloading pump
08G14D | Agitator for 08T9D
08G14D | Agitator for 08T9D
08G1A | Fatty acid unloading pump
08G1B | Fatty acid unloading pump
08G1C | Fatty acid unloading pump
08G20 | Intermediate Transfer Pump
08G21 | Intermediate Transfer Pump
08G22 | Intermediate Transfer Pump
08G23 | Intermediate Transfer Pump
08G24 | Intermediate Transfer Pump
08G25 | Intermediate Transfer Pump
08G2A | Fatty acid transfer pump
08G2B | Fatty acid transfer pump
08G3A | Fatty Alcohol product filling pump
08G3B | Fatty Alcohol product filling pump
08G3C
08G4A | Wax transfer pump
08G5A | Intermediate FA transfer pump
08G5B | Intermediate FA transfer pump
08G6A | Light end filling pump
08G7A | Residue filling pump
08G8A | Naphtha transfer pump
08G8B | Naphtha transfer pump
08G9A | Naphtha transfer pump Vertical
08N14A | Agitator for 08T9A
08N14B | Agitator for 08T9B
08N14C | Agitator for 08T9C
08N14D
08N15A | Agitator for 08T007
08N16A | Agitator for 08T005
08N17A | Agitator for 08TGA
08N17B | Agitator for 08TGB
08N17C | Agitator for 08TGC
08N17D | Agitator for 08TGD
08N17E | Agitator for 08T4E
08N18A | Agitator for 08T3A
08N18B | Agitator for 08T3B
09G2 | Soap pump for process
09G3 | Soap pump for process
09G4 A | Effluent transfer pump
09G4 B | Effluent transfer pump
09G4 C | Effluent transfer pump
09G5 | Effluent transfer pump
09U1D14 | Centrifuge
09U1G10 | pH Correction Tank Agitator
09U1G11A | HRSCC Feed Pump A
09U1G11B | HRSCC Feed Pump B
09U1G12 | pHCT Agitator
09U1G13A | Centrifuge feed pump- A
09U1G13B | Centrifuge feed pump- B
09U1G14A | Bio Tower Feed Pump A
09U1G14B | Bio Tower Feed Pump B
09U1G15A | Bio Tower Recirculation - A
09U1G15B | Bio Tower Recirculation - B
09U1G16A | Air Blower 16-A
09U1G16B | Air Blower 16-B
09U1G17 | Air Blower
09U1G1A | Heat Exchanger Feed Pump-A
09U1G1B | Heat Exchanger Feed Pump-B
09U1G20 | C-MEM A Water Transfer Pump
09U1G21 | Process Water Transfer pump
09U1G22 | C-MEM B Water Transfer Pump
09U1G23 | C-MEM A Backwash Pump
09U1G24 | C-MEM B Backwash Pump
09U1G25 | RO Cartridge feed Pump
09U1G26 | RO High Pr. Pump
09U1G27 | RO Permeate Transfer Pump
09U1G28 | RO Cleaning Soln. Pump
09U1G29A | Lime Dosing Pump- A
09U1G29B | Lime Dosing Pump- B
09U1G2A | Lamella Feed Pump A
09U1G2B | Lamella Feed Pump B
09U1G3 | Flash Mixer 4A
09U1G30 | Lime Tank Agitator
09U1G32 | FeCl3Dosing Tank Agitator
09U1G35 | Polymer Dosing tank Agitator
09U1G36B | Acid Doasing Pump B
09U1G38 | Deoiling Polymer tank Agitator
09U1G39 | PAC Dosing Pump
09U1G4 | Flocculator Tank Agitator 4B
09U1G41 | Nutrient Dosing Pump
09U1G42 | Nutrient Dosing tank Agitator
09U1G43 | NaOCl Dosing Pump
09U1G44 | Organic Clining Doasing Pump
09U1G45 | Organic Clining tank Agitator
09U1G51 | Cleaning Soln. Tank Agitator
09U1G52 | Dewatering Polymer Dosing Pump
09U1G53 | Dewatering Polymer Tank Agitator
09U1G54 | NaOH Dosing Pump
09U1G55 | NaOH Tank Agitator
09U1G5A | DAF FeedPump - A
09U1G5B | DAF FeedPump - B
09U1G6 | Flash Mixer Tank Agitator 7A
09U1G7 | Flocculator Tank Agitator 7B
09U1G8 | Air compressor
09U1G9 | DAF High Pr. Pump
09U2G1A | Effluent transfer pump
10G01A | F.D.Fan
10G01B | F.D.Fan
10G01C | F.D.Fan
10G02 | Recycle H2 Compressor
10G03A | Naphtha feed pump
10G03B | Naphtha feed pump
10G04A | BWF pumps
10G04B | BWF pumps
10G05 | Naphtha condensate pump
10G15B
10U2G1 | TNP Dosing pump
10U2G2 | Na2S Dosing pump
10U2G3 | Mixer for phosphat tank
10U2G4 | Mixer for Hydrozen tank
14G01A | Alcohol feed pump
14G02A | Alcohol feed pump
14G03A | Alcohol feed pump
14P01A | Storage tank area
14P01B | Fatty acid pump-1
14P01C | Fatty acid pump-2
14P01D | Fatty acid pump-3
14P02A | Caustic unloading pump
14P02B
14P04A | Caustic unloading pump - 3
14P04B | Caustic soda transfer pump from PIT
14P05 | Slop sump pump
14P07 | caustic unloading pump
20P01 | Hot well pump
20P02A | Cold well pump
20P02B | Cold well pump
20P03A | Cooling water pump-1
20P03B | Cooling water pump-2
20P04A | Cooling water pump-3
20P05A | Cooling water pump-4
20P07A | Raw water pump-1
20P07B | Raw water pump-2
20U01A | Chilled water pump
20U03B01 | Cooling tower fan-3
20U04A01 | Cooling tower fan-1
20U04B01 | Cooling tower fan-2
20U05B01 | Blower for side stream filter
22P1A | Condensate transfer pump B
22P1B | Condensate transfer pump A
23P02
23-P1 | Effluent transfer pump
A-651A | Agitator
A-651B | Agitator
A-651C | Agitator
A-704 | Mixer
AG-7106 | BATCH BLEACHER AGITATOR
AG-7110 | ATFD STIRRER
AG-801
AG-802
AGITATOR | Agitator motor
B-150.1 | Centrifugal fan
B-250.8A | Automatic cleaning bag filter
BDG-1
BDG-2
C-103A | Recycle compressor
C-103B | Recycle compressor
C-128.1 | Washing column feed pump
C-301 | cooling water pump -1
C-302 | cooling water pump -2
C-303 | cooling water pump -3
C-401 | PUMP
C-402 | PUMP
C-403 | PUMP
C-901 | Post cooler chain conveyor
C-902 | Rotoform Ist pastillator
C-903 | Steel belt conveyor
C-904 | conveyor No 1
C-905 | conveyor No 2 (wood steeper)
C-906 | conveyor No 3(metal detector)
C-907 | Conveyer no.4(Bag rejector)
catalyst hoist motor
CH-7000A
CH-7000B
CT FAN-1 | CT FAN-1 JUTASAMA
CT FAN-2 | CT FAN-2 JUTASAMA
CT FAN-3 | CT FAN-3 K3'
CT-903A-F | Cooling tower fan
CT-903B-F | Cooling tower fan
CT-903C-F | Cooling tower fan
D-1-1 | Hotwell pump
D-117.2 | Tinipal feed tank
D-117.3 | Super fat feed pump
D-1-2 | Hotwell pump
D-150.5 | Intermediate collecting tank
D-150.6 | Intermediate collecting tank
D-201.1 | Soap feed pump
ETP Homogeneous Dosing tank agitator | ETP Homogeneous Dosing tank agitator
ETP Homogeneous tank-B motor | ETP Homogeneous tank-B motor
F/P-I | 1st Treated Sweet Water Filter Press
F/P-II | 2nd Treated Sweet Water Filter Press
F/P-III | 3rd Treated Sweet Water Filter Press
F-101 | ID fan
F-102 | FD fan
F-150.1A | Filter press for basic filteration A
F-150.1B | Filter press for basic filteration B
FD-308 | NEW FLAKER DRUM 1 MOTOR
FD-309 | NEW FLAKER DRUM 1 MOTOR
FD-310 | CONVEYOR MOTOR
FL-101 | Flaker
G11B M 01 | Dosing pump
G20 M01 | Dosing pump
IAEC boiler feed water pump-2
lindhe plant | Dosing pump-2
LP-118
P-01 | Hot well pump
P-100A1 | Naphta feed pump
P-100A2 | Naphta feed pump
P-100B1 | Naphta feed pump
P-100B2 | Naphta feed pump
P-101 | Transfer pump
P-101 | High pressure pump
P-101.6 | Hot water pump
P-101A | BFW pump
P-101B | BFW pump
P-102 | High pressure pump
P-102.1 | Hydro sulphite solution pump
P-103 | Hot oil circulation pump
P-103 | High pressure pump
P-104 | Water ring vacuum pump
P-104.1 | EDTA Dosing Pump
P-104A | Feed pump Oil to V- 101
P-104B | Feed pump Oil to V- 101
P-104C | Feed pump Jutasama
P-104D | Feed pump Jutasama
P-105 | Cooling water transfer pump
P-105A | Water Feed Pump
P-105B | Water Feed Pump
P-106A | Split Fatty Acid Transfer Pump
P-106B | Split Fatty Acid Transfer Pump
P-107A | Crude OIl CIrculation Pump
P-107B | Crude OIl CIrculation Pump
P-109 | Collected oil transfer pump
P-114B
P-117.2 | Tinopal dosing pump
P-117.3 | Superfat doasing motor
P-117.4 | Giycerine doasing pump
P-121.3A | NACI solution recycle pump
P-121.3B | NACI solution recycle pump
P-122.2 | Caustic soda transfer pump
P-124.3 | Soap transfer pump
P-124.6 | Lye transfer pump
P-124.7 | Soap transfer pump
P-128.10 | Centrifuge feed pump
P-128.12A | Soap to storage pump
P-128.12B | Soap to storage pump
P-128.15 | Soap Recycle pump
P-128.1A | Fat feed pump-1
P-128.1B | Fat feed pump-2
P-128.1C | Fat feed pump-3
P-128.2 | Brine feed pump
P-128.21 | Vaccum pump
P-128.3 | Caustic soda feed pump
P-128.5 | Nutralization agent feed pump
P-128.6A | Reactor recyle pump
P-128.6A | Seal water pump
P-128.7 | Static separator feed pump
P-128.8 | Washing column feed pump
P-128.9 | Column lye reactor pump
P-14A | E-103 thermic fluid circulation pump
P-14B | E-103 thermic fluid circulation pump
P-150.1 | Spent lye feed pump
P-150.2 | Filteration pump
P-150.3 | Mixer feed pump
P-150.4 | Filteration pump
P-150.5 | HCL acid dosing pump
P-150.6 | Coagulant dosing pump
P-150.7 | Caustic soda dosing pump
P-150.8 | Caustic soda recycle pump
P-150.9 | Feeding soap lye pump
P-168.1A | Cool(Spent lyes feed pump)
P-168.10 | Crude glycerine extraction pump
P-168.11 | Centrifugal pump for con. Rec.
P-168.1A | Vaccum filter motor 1
P-168.1B | Vaccum filter motor 1
P-168.1C | Vaccum filter motor 1
P-168.1D | Vaccum filter motor 1
P-168.2 | First effect recycle pump
P-168.2B | S/W circulation Pump
P-168.3 | Second effect recycle pump
P-168.3B | S/W circulation Pump
P-168.4 | Condensate pump
P-168.4B | S/W circulation Pump
P-168.5 | Crude glycerine extration pump
P-168.5B | Crude Gly. Transfer Pump
P-168.6 | Centrifugal pump for brine
P-168.7 | Liquid wing vaccum pump
P-168.9 | Filtrate pump from S168.1
P-180.1 | Coagulant transfer pump
P-180.1A | Coagulant transfer pump
P-180.2 | Coagulant transfer pump
P-180.4 | C.P. glycerine storage
P-200.1 | Soap filteration pump
P-201 | High Pressure Fat Feed Pump
P-201 | Forced Cooling fan for p-201
p-201A
P-202 | High Pressure Fat / Water Feed Pump
P-202 | Forced Cooling fan for p-202
P-203 | Water Charge Pump.
P-203 | Forced Cooling fan for p-203
P-203.1 | Silicate feed pump
P-205A | Water Feed Pump
P-205B | Water Feed Pump
P-206.1 | Vaccum pump
P-206.2 | Hot well pump -1
P-206.3 | Hot well pump -2
P-206A | Fatty Acid Circulation Pump
P-206B | Fatty Acid Circulation Pump
P-208A | Fat Circulation Pump
P-208B | Fat Circulation Pump
P-209 | Collected oil transfer Pump
P-2601A | Thermic fluid circulation pump
P-2601B | Thermic fluid circulation pump
P-27A | Water ring vacuum pump
p-27B | Water ring vacuum pump
P-29A | K-3 Reboiler circulation pump
P-29B | K-3 Reboiler circulation pump
P-303A | C6/C8 transfer pump-1
P-303B | C6/C8 transfer pump-2
P-304A | C10/12 transfer pump-1
P-304B | C10/12 transfer pump-2
P-305A | C8/C10 transfer pump-1
P-305B | C8/C10 transfer pump-2
P-306A | C12/C14 transfer pump-1
P-306B | C12/C14 transfer pump-2
P-307A | Reboiler circulation pump-1
P-307B | Reboiler circulation pump-2
P-308A | Reboiler circulation pump-1
P-308B | Reboiler circulation pump-2
P-309A | Bottom product transfer pump-1
P-309B | Bottom product transfer pump-2
P-30A | K-3 bottom product transferring pump
P-30B | K-3 bottom product transferring pump
P-30C | K-3 bottom product transferring pump
P-310A | Bottom product transfer pump-1
P-310B | Bottom product transfer pump-2
P-311A | Hot oil circulation pump-1
P-311B | Hot oil circulation pump-2
P-312A | Hot oil circulation pump-1
P-312B | Hot oil circulation pump-2
P-313A | Dryer circulation pump-1
P-313B | Dryer circulation pump-2
P-314A | LE transfer pump-1
P-314B | LE transfer pump-2
P-317A | SFA feed pump-1
P-317B | SFA feed pump-2
P-318A | Hot oil dooster pump-1
P-318B | Hot oil dooster pump-2
P-31A | E-13 Condensate transferring pump
P-31B | E-13 Condensate transferring pump
P-320A | Oil circulation pump-1
P-320B | Oil circulation pump-2
p-320D
P-322A | Direct CW pump-1
P-322B | Direct CW pump-2
P-323A | Effluent transfer pump
P-323B | Effluent transfer pump
p-323C
p-323D
P-324A | Condensate pump-1
P-324B | Condensate pump-2
P-326A | Cooling water pump-1
P-326B | Cooling water pump-2
P-327A | Oil transfer pump to storage tank
P-32A | M/D transferring pump
P-32B | M/D transferring pump
P-32C | M/D transferring booster pump
P-33A | E-12 thermic fluid circulation pump
P-33B | E-12 thermic fluid circulation pump
P-34A | D-20 DM water V-303
P-34B | D-20 DM water V-303
P-350A | New k3' feed
P-350B | New k3' feed
P-351A | Dehydrator circulation Pump
P-351B | Dehydrator circulation Pump
P-352A | L/E Transfer Pump of Dehydrator
P-352B | L/E Transfer Pump of Dehydrator
P-353A | Hot oil circulation Pump (preheater)
P-353B | Hot oil circulation Pump (preheater)
P-354A | Bottom recirculation pump
P-354B | Bottom recirculation pump
P-355A | B/P Pump K3'
P-355B | B/P Pump K3'
P-356A | Hot oil circulation Pump (reboiler)
P-356B | Hot oil circulation Pump (reboiler)
P-357A | Pump around system pump
P-357B | Pump around system pump
P-358A | L/E Transfer Pump of C-303
P-358B | L/E Transfer Pump of C-303
P-359A | Side draw transfer pump of C-303
P-359B | Side draw transfer pump of C-303
P-360A | Hotwell Pump
P-360B | Hotwell Pump
P-361A | Tempered water pump
P-361B | Tempered water pump
P-362A | Cooling water pump-K3'
P-362B | Cooling water pump-K3'
P-362C | Cooling water pump-Jutasama
P-362D | Cooling water pump-Jutasama
P-363A | DM water pump
P-363B | DM water pump
P-364A | Clean CW Pump -Precon & Postcon
P-364B | Clean CW Pump -Precon & Postcon
P-365A | Dirty Water Pump
P-365B | Dirty Water Pump
P-36A | K-3 Reboiler thermic fluid circulation pump
P-36B | K-3 Reboiler thermic fluid circulation pump
P-3A | Feed pump to D-10
P-3B | Feed pump to D-10
P-402A | LE transfer pump-1
P-402B | LE transfer pump-2
P-407A | Residue transfer pump-1
P-407B | Residue transfer pump-2
P-409A | LE transfer pump fromV-403-1
P-409B | LE transfer pump fromV-403-2
P-410A | Bottom circulation pump for C-402-1
P-410B | Bottom circulation pump for C-402-2
P-411A | Hot oil transfer pump for ER-402-1
P-411B | Hot oil transfer pump for ER-402-2
P-412A | Distillate transfer pump-1
P-412B | Distillate transfer pump-2
P-414A | HFA transfer pump-1
P-414B | HFA transfer pump-2
P-418A | Hot oil booster pump-1
P-418B | Hot oil booster pump-2
P-419A | SFA feed pump-1
P-419B | SFA feed pump-2
p-419C
P-420A | Hot oil transfer pump -1
P-420B | Hot oil transfer pump -2
P-421A | L/E transfer pump
P-421B | L/E transfer pump
P-422A | Direct cooling water return pump-1
P-422B | Direct cooling water return pump-2
p-422C | Thermic fluid pump
P-422D | Thermic fluid pump
P-423B
P-423C
P-423D | Column 401 reboiler circulation pump
p-424A
P-424B
P-426A | Internal Circulation Pump
P-426B | Internal Circulation Pump
P-430A | ICW circulation pump-1
P-430B | ICW circulation pump-2
P-430C | ICW circulation pump-3
P-431A | Dryer Circulation Pump
P-431B | Dryer Circulation Pump
P-450A | New SPD feed
P-450B | New SPD feed
P-451A | Motor For Dehydrator Pump P-451A
P-451B | Motor For Dehydrator Pump P-451B
P-452A | Motor For Steam Separator P-452A
P-452B | Motor For Steam Separator P-452B
P-453A | Motor For Thermic Fluid Circulation preheater P-453A
P-453B | Motor For Thermic Fluid Circulation preheater P-453B
P-454A | Motor For SPD main distillate P-454A
P-454B | Motor For SPD main distillate P-454B
P-455A | Motor For SPD Bottom P-455A
P-455B | Motor For SPD Bottom P-455B
P-456A | Motor For Hot well Circulation P-456A
P-456B | Motor For Hot well Circulation P-456A
P-457A | Motor For Thermic Fluid water Circulation Reboiler P-457A
P-457B | Motor For Thermic Fluid water Circulation Reboiler P-457B
P-4A | D-10 to K-3
P-4B | D-10 to K-3
p-510A
P-511A | Bottom circulation pump
P-511B | Bottom circulation pump
P-512A | Bottom draw pump
P-512B | Bottom draw pump
P-513A | Hot oil circulation pump
P-513B | Hot oil circulation pump
P-514A | Distillate transfer pump
P-514B | Distillate transfer pump
P-515A | Pump for steam generator
P-515B | Pump for steam generator
P-516A | Light end transfer pump
P-516B | Light end transfer pump
P-517A | SPD Distilate Transfer Pump
P-517B | SPD Distilate Transfer Pump
P-518A | SPD Distilate Residue Transfer Pump
P-518B | SPD Distilate Residue Transfer Pump
p-518C
P-519A | Thermic fluid pump
P-519B | Thermic fluid pump
P-520 | Feed pump for SPD
P-522 | Vaccum pump
P-523 | Feed pump
p-551B
P-602A | High Pressure Fat / Water Feed Pump
P-602B | High Pressure Fat / Water Feed Pump
P-604A | Crude Sweet Water Transfer Pump
P-604B | Crude Sweet Water Transfer Pump
P-604C | CRUDE SWEET WATER TRANSFER PUMP
P-605 | Decanted oil transfer pump
P-606 | Fatty Acid Circulation Pump
P-607 | Fat Circulation Pump
P-608 | Fat Circulation Pump
P-610 | Skimmed oil transfer pump
P-651A | Feed Pump
P-651A | Product x'per pump
P-651B | Feed Pump
P-652 | Transfer/Recirculation
P-652A | Hot water x'per pump-1
P-652B | Hot water x'per pump-2
P-653 | Transfer/Recirculation
P-653A
P-653B | C.W.R.Pump(Pastillator Ground Floor)
P-654 | Transfer/Recirculation
P-655 | Product Pump
P-656A | Condensate Pump
P-656B | Condensate Pump
P-657A | Condensate Pump
P-657B | Condensate Pump
P-658 | pump nr to p-9002A
P-685 | Hot Oil Pump
P-686 | Crude Glycerin Transfer pump
P-687 | Hot Well pump
P-688 | Sweet water hot well pump
P-689 | Precon Sweet water pump
P-702 A | vessel 702 bottom circulation pump
P-702B | vessel 702 bottom circulation pump
p-703A/B
P-704A | Finish Material Tr. Pump
P-704B | Finish Material Tr. Pump
P-705 | Circulation Pump
P-706A | D.M. Water Pump
P-706B | D.M. Water Pump
P-707B
P-7100A | TANK FORM FEED PUMP
P-7100B | TANK FORM FEED PUMP
P-7101 | CRUDE RECIRCULATION PUMP
P-7102 | DEODERIZER DRYER RECIRCULATION PUMP
P-7103A | FEED PUMP
p-7103B | FEED PUMP
P-7104A | RESIDUE TRANSFER PUMP
P-7104B | RESIDUE TRANSFER PUMP
P-7106 | DISTILLATE PUMP
P-7107 | BLEACHER FEED PUMP
P-7108 | SUB STANDARD GLYCERINE TRANSFER PUMP
P-710A | Vaccum Pump
P-710B | Vaccum Pump
P-7110A | PITCH PUMP
P-7110B | PITCH PUMP
P-7111 | INTERMEDIATE DISTILLED GLYCERINE X-MER PUMP
P-7112 | FLASH VESSEL-II
P-7113 | X-FER PUMP FROM ATFD RECEIVER
P-7114A | X-FER PUMP FROM HOT WELL TO COOLING WATER
P-7114B | X-FER PUMP FROM HOT WELL TO COOLING WATER
P-7115A | COOLING TOWER X-FER PUMP-1
P-7115B | COOLING TOWER X-FER PUMP-2
p-7117 | INTERMEDIATE REFINED GLYCERINE X-FER PUMP
p-7118 | FIRST STAGE FLASH PUMP
P-7119 | SECOND STAGE FLASH PUMP
P-711A | Loop-1
P-711B | Loop-2
P-711C | Loop-3
P-7120 | ATFD FEED PUMP
P-7121 | SCRUBBER CIRCULATION PUMP
P-7122
p-7123 | HOT OIL X-FER PUMP FOR E-102
P-7124 | HOT OIL FOR ATFD
P-7125 | SCRUBBER DISCHARGE PUMP
P-7126A | SCRUBBER CIRCULATION PUMP
P-7126B | SCRUBBER CIRCULATION PUMP
P-7126C | SCRUBBER CIRCULATION PUMP
P-7126D | SCRUBBER CIRCULATION PUMP
P-7127A | FINISHED GOOD LOADING PUMP
P-7127B | FINISHED GOOD LOADING PUMP
P-7128 | PIT PUMP
P-755B
P-757A
P-765 | Bottom circulation pump
P-795 | Vaccum Pump
P-8001A | Condensate Transfer Pump
P-8001B | Condensate Transfer Pump
P-801A | Trolly Unloading Pump-1
P-801B | Trolly Unloading Pump-2
P-801C | TROLLY UNLOADING PUMP-3
P-801D | TROLLY UNLOADING PUMP-4
P-801E | TROLLY UNLOADING PUMP-5
P-801F | TROLLY UNLOADING PUMP-6
P-802A | Crude oil transfer pump-1
P-802B | Crude oil transfer pump-2
P-802C | Crude oil transfer pump-3
P-802C | Crude oil transfer pump-3
P-803 | FEED PUMP
P-804A | Feed for C-301/302
P-804B | Feed for C-301/302
P-806A | C12 LAURIC/PKD unloading pump-1
P-806B | C12 LAURIC/PKD unloading pump-2
P-807A | C12 LAURIC/PKD transfer pump-1
P-807B | C12 LAURIC/PKD transfer pump-2
P-808A | Old K3/k4 feed
P-808B | Old K3/k4 feed
P-809 | Feed alcohol
P-811A | 401/402 Feed pump
P-811B | 401/402 Feed pump
P-812B | Distilled FPAD/CPS transfer pump
P-813A | Heavy end transfer pump-1
P-813B | Heavy end transfer pump-2
P-815 | Glycerine transfer pump
P-816A | Oil fat trap pump
P-816B | Oil fat trap pump
P-817A | Old K3/k4 feed
P-817B | Old K3/k4 feed
P-818 | ISO LOADING PUMP
P-819A | Feed for splitting/lurgi
P-819B | Feed for splitting/lurgi
P-820 | Oil dhakka circulation pump
P-820 | Loading Unloading pump
P-821 | Loading Unloading pump
P-821A | Oil dhakka circulation pump
P-821B | Oil dhakka circulation pump
P-822A | Alcohol feed
P-822B | Alcohol feed
P-823 | Oil dhakka circulation pump
P-824 | Oil dhakka circulation pump
P-825A | Bleacher
P-825B | Bleacher
P-825C | Bleacher
P-825D | Bleacher
P-826 | Drum filling
P-827 | Oil dhakka circulation pump
P-828 | Oil dhakka circulation pump
P-829 | Oil dhakka circulation pump
P-830A | Old K3 feed
P-830B | Old K3 feed
P-831 | Vent condensate xfer pump
P-832 | Pump for settling tank
p-833
P-9002A | CW supply Pump for Splitting & SW
P-9002B | CW supply Pump for Splitting & SW
P-901A | Tempered water pump
P-901B | Tempered water pump
P-903A | Indirect cooling water pump-1
P-903B | Indirect cooling water pump-2
P-903C | Indirect cooling water pump-3
P-903D | Indirect cooling water pump-4
P-905A | Fo transfer pump
P-905B | Fo transfer pump
P-906A | RW transfer pump
P-906B | RW transfer pump
P-906C | RW transfer pump
P-908 | D.M.Water transfer pump
P-909 | Intermediate pump for mp boiler
P-910A | Cooling water return pump
P-910B | Cooling water return pump
P-913 | WTP Pump-1
P-913 | WTP Pump-1
P-914 | Filtered water booster pump
P-919A | D.M.Water transfer pump-1
P-919B | D.M.Water transfer pump-2
P-920 | Blowdown transfer pump
P-951A | Chilling water transfer pump-1
P-952A | Chilling water transfer pump-2
P-953A | Chilled water secondry Pump
P-953B | CHW secondary stnd by pump for P953A
P-954A | Chiller compressor
P-955
P-961
P-962
P-963
P-964
P-965
P-966
P-967A
P-967B
P-CD100 | Clean condensate Pump
PL-204.1 | Twin warn simplex refiner
PS-102.1 | Hydro sulphite solution pump
PS-104.1 | EDTA solution mixer
PS-168.1 | Salt dessalving mixer
R-101 | Reactor Agitator
R-102 | Bleacher Agitator
R-128.2 | Terbo disperser pump
S-128.2A | Centrifugal separator
S-128.2B | Centrifugal separator
S-128.2B | Soap mixer
S-128.2C | Centrifugal separator
S-509 | Stirrer for SPD
S-D204.1 | Vaccum sprey chamber
SPD450 | Motor For Agitator SP-D450
T-150.1A | Talc system
T-150.1B | Talc system
T-205.1 | Soap fins warm conveyor
T-205.1A | Soap fine warm conveyor
T-205.2 | Soap fins warm conveyor
T-205.2A | Soap fins warm conveyor
TF-12A | Feed for C-401/402
TF-12B | Feed for C-401/402
TF-33A | LOOP FEED PUMP
TF-33B | Feed for C-301/303
TF4-32A | FEED TO FLAKER-1
TF4-32B | FEED TO FLAKER-2
TF4-32C | FEED TO FLAKER-3
T-SC02 | Talc Screw Conveyer
V-101 | Charger Agitator
VP-27 B | NEW VP NEAR VP-27,K3
VP-351A | Vac. Pump
VP-351B | Vac. Pump
VP-451 | Motor For Vaccum Pump VP-451
VP-651A | Vacuum Pump
VP-651B | Vacuum Pump
VP-7103A | VACCUM PUMP-1
VP-7103B | VACCUM PUMP-2
VPX-601A | Water ring vacuum pump
VPX-601b | Water ring vacuum pump
VP-X-689 | Vacuum pump
X-101A | vacuum Pumps (Water Ring)
X-101B | VACUUM PUMP
X-201 | VacuumPump
X-301-1 | Vaccum pump
X-401-1 | Vaccum pump-1
X-401-2 | Vaccum pump-2
Belt converyor
CROSS TRAVEL
CROSS TRAVEL
Glvcrin Pump
Scew conveyor
Vaccum pump
HOIST 1
Buckhardt Compressor
De-watering pump Weigh-Bridge
De-watering pump tankfarm area
HOIST 2
De-watering pump main plant
Filter Press Moter A
Filter Press Moter B
HRSCC Recirculation
HRSCC Scapper
Rotadal TPI Oil Remover Pump
Condensate Transfer Pump
ATLAS Cpco comp. fan motor
Thermic Fluid F.D.Fan
Ring main pump-1
Ring main pump-2
Chemical dosing pump
Chemical tank Agitator motor
Thermic fluid transfer pump
Oil pump no.1
Oil pump no.2
De-watering pump hot oil
ETP To Cooling Tower Tr. Pump
Agitator - 1
back ceiling CONVER BELT NO-1
Sewing Head Motor
INFEED MOTEF
back ceiling CONVER BELT NO-2
Sewing Head Motor
INFEED MOTEF
TF-3/AGITATOR-MOTOR
Agitator - 2
conveyor-2
Blower
cold well pump
chiller
new flaker drum-1
conveyor-1
new flaker blower
conveyor-3 (1st floor)
Sealing machine
Lifting belt conveyor
HOT WELL PUMP
Hydralic motor
new flaker drum-2
Sealing Belt Motor
Sewing Head Motor
AHU Motor (1st Floor Pastillator)
Fridge fan blower
Blower
Guttar Pump
Feed Pump flacker
New Flakar C.W.R.Pump
VAPOUR BOILER - 1
VAPOUR BOILER - 2
BELT CONVEYOR PAST.GROUND FLR
STEEL BELT CONVEYOR BLOWER
K3 CT fan
Extract Pump
oil remover motor
Water recycle pump
AGITATOR-1 NEAR TANK-824
AGITATOR NEAR TANK-803
New Flakar Drum Motor
AGITATOR-1 NEAR TANK-821
03G16A
03G18A
03G18B
P-1000 | FAF BLOWER
P-1001A | AUX.AIR FAN A
P-1001B | AUX.AIR FAN B
P-1002 | AUX.AIR FAN 1
P-1003 | GULLOTINE DAMPER G5_01
P-1004 | GULLOTINE DAMPER G5_02
P-1005 | GULLOTINE DAMPER G5_03
P-1006 | SAF GD-01
P-1007 | SAF GD-02
P-1008 | SAF GD-03
P-1009 | SAF FD-01
P-1010A | BOILER FEED WATER PUMP-A
P-1010B | BOILER FEED WATER PUMP-B
P-1011A | THERMIC FLUID PUMP-A
P-1011B | THERMIC FLUID PUMP-B
P-1012A | COOLING WATER PUMP-A
P-1012B | COOLING WATER PUMP-B
P-1012C | COOLING WATER PUMP-C
P-1013A | CHILLED WATER PUMP-A
P-1013B | CHILLED WATER PUMP-B
P-1013C | CHILLED WATER PUMP-C
P-1014A | STARTUP VENT S24
P-1014B | STEAM SUPPLY S25
P-1015A | HOT WATER PUMP-A
P-1015B | HOT WATER PUMP-2
P-1016A | CT FAN-1
P-1016B | CT FAN-2
P-1017A | COOLING WATER GT PUMP-A
P-1017B | COOLING WATER GT PUMP-B
P-1018A | AIR COMPRESSOR-A
P-1018B | AIR COMPRESSOR-B
P-1019A | LP DOSING PUMP-A
P-1019B | LP DOSING PUMP-B
P-1019C | LP DOSING AGITATOR
P-1020A | HP DOSING PUMP-A
P-1020B | HP DOSING PUMP-B
P-1020C | HP DOSING AGITATOR
P-1021 | MAKEUP WATER PUMP
VAM-1 | VAM-1
VAM-2 | VAM-2
P-1022 | CONDENSATE TRANSFER PUMP
Pit-Pump-1
Pit pump-2
P-1023 | HOT WATER PESTILLATOR -1
P-1024 | HOT WATER PESTILLATOR -2
101.7 | Dirty cooling water return pump
P-1302 | Chilled water Pump
P 117.5 | Alcohol Transfer Pump
PLD 1301 | Plodder
P 128.2 | Condensate Transfer Pump
P 118.5 | Alc Transfer pump
VP 1301A | Vaccum Pump
VP 1301B | Vaccum Pump
CD-1301 | Chilled Drum
Conveyer Blet
Hydrolic Pack
MS 1307 | Multi Screw
BL 1301 | Blower
PSC 1301 | Scrubber Circulation Pump
P-T-1301 | Ester Vessel Transfer Pump
P-T-1302 | Sulphonification vessel
T 1301 | Esterification vessel
T 1302 | Sulphonification vessel
T 1304 A | Turbo Mixer 1
T 1304 B | Turbo Mixer 1
Note on A399: NOT IN USE
Note on A400: NOT IN USE
Note on A401: NOT IN USE
Note on A402: NOT IN USE