## Report
Reliability Improvements at Taloja Plant
The project was initiated in the first week of June, 2016. It was aimed at followings. 1. Identify the areas of reliability improvements 2. Basic analysis of identified areas of reliability improvements 3. Conduct sessions on reliability improvements - equipment specific or parameter specific 4. Identify vendors and receive offers for the gadgets / instruments / software that can help on reliability improvement 5. Conduct demo for use of identified instruments / software 6. Generate Capex proposals for reliability improvements
1. Identify the areas of reliability improvements
Based on history of failures, Taloja maintenance team has identified following areas of reliability improvements. 1. Heat Exchangers 2. Cooling Towers 3. Pumps, Fans & Rotating machineries 4. Critical equipment Foundations & Plant Structure
2. Basic analysis of identified areas of reliability improvements
1. Heat Exchangers: Fatty Acid plant heat exchangers failure analysis started in the year 2015. 37 heat exchangers from fatty acid Taloja and 15 heat exchangers from fatty acid Baddi (Enlisted below) were identified and enquiry floated to M/s Alfa Laval and M/s Kelvion. Based on operating parameters like, flow rate, pressure drop, heat transfer duty, operating temperatures and foot print, 7 universal heat exchangers were identified. Following was the concept of the universal heat exchanger. Each of the seven universal heat exchangers is useful for a defined set of heat exchanger at Taloja and baddi. Whenever there is a failure of one of the defined set of heat exchanger, the corresponding universal heat exchanger to be placed on removal of leaking heat exchanger. This will save on heating / cooling load and maintain the process efficiency. The removed heat exchanger is either repaired or replaced by new one. On receiving repaired / new heat exchanger, remove the universal heat exchanger and place the original /new heat exchanger. Annexure 2.1 contains the details of the universal heat exchangers. The same are procured and kept ready for use at any point of time by Baddi or Taloja Plant
VVF'S Tag No | Sr. No. | Type
Taloja Plant DFA Heat exchangers considered for universal Hess
E-453( FA Vs Steam) | 30113-76205 | 1V-C-1C
E-501(FA Vs Steam) |  | 1V
E-354 (FA Vs Steam) | 30112-76377
E-305(FA Vs Water) | 31000-01-540 | 1H
E-306(FA Vs Water) | 31000-01-540
E-407A (FA Vs Water) |  | 1H
E-402 (FA Vs FA) | TSN 000234 | 1H
E-409 (k4 B/P COOLER- FA Vs Water) | 31000-01-5
E-310 (FA Vs FA) | 31000-01-530 | 1H-L-1T
E-351B/E-201 (FA Vs Water) | 30115-86823 | 1H-L-1T
E-311 (FA Vs FA) | 31000-01-531 | 1H-L-1T
E-314 Compablock (FA Vs Water) |  | CPL30-V-132
E-362 (FA Vs Water) | 31000-02-764 | 1H-L-1T
E-521A & B (FA Vs FA- Eurucic acid) | 31000-02-561/562 | 1H-L-1T
E-102 (FA Vs FA) |  | 1H
E-406 A (FA Vs FA)
E-309 (FA Vs Water) | 31000-01-529 | 1H-L-1T
E-457 (FA Vs Water) | 30113-76208
E-458 (FA Vs Water) | 30113-76209
E-360 (FA Vs Water) | 30113-76337
E-410 / E-301 Compablock | CP40-1031 | CPK40-V-200
E-313A (FA Vs Water) |  | 1H-L-1T
E-426 (FA Vs FA) | 31000-01-890 | 1H-L-1T
E-428 (FA Vs Water)
E-425 (FA Vs Water)
E-351 A (FA Vs FA)
E-358 ( FA Vs FA) | 31000-02-767 | 1H-L-1T
E-353 (FA Vs FA) | 31000-02-768 | 1H-L-1T
E-352 (FA Vs FA) | 31000-02-765 | 1H-L-1T
E-451 (FA Vs FA) | 30113-76203 | 1H-L-1T
E-104 (FA Vs FA) | 31000-02-498 | 1H-L-1T
E-105 (FA Vs FA) | 31000-02-497 | 1H-L-1T
E-101 (FA Vs FA) |  | 1H
E-452 (FA Vs FA) | 30113-76204 | 1H-L-1B
E-435 (FA Vs FA) | 31000-01-897
E-454 (FA Vs FA) | 30113-76206 | 1H-L-1B
E-357 (FA Vs FA) | 31000-02-766 | 1H-L-1T
Baddi Plant DFA Heat exchangers considered for universal Hess
E-101 A (Feed Oil Vs CFA)
E-101 B (Feed Oil Vs CFA)
E-101 C (Feed Oil Vs CFA)
E-102 (Steam Vs Feed Oil)
E-103 (CFA Vs Water)
E-301 (CFA Vs LPS) | 7PC-D-626 | SHELL & TUBE
E-302 (CFA Vs Main DFA of D3) | NU-2034 | SPIRAL
E-303 (CFA Vs Thermic Fluid) | 7PC-D-627 | SHELL & TUBE
E-304 (CFA Vs L/E of D2) | 280762 | PLATE
E-305 (CFA Vs Residue of D3) | NU-2035 | SPIRAL
E-314 (CW Vs Main DFA of D3) | 280763 | PLATE
E-314A (CW Vs Main DFA of D3) | 280763 | SPIRAL
E-315 (CFA Vs Main DFA of D3) | 280764 | PLATE
E-317 (CW Vs L/E of D2) | 280765 | PLATE
E-320 (Water Vs Water)
2. Cooling Towers: At Taloja Plant, the cooling towers are installed over a period of 2004 till date based on the requirements of greenfield or brownfield projects. This is most neglected area of maintenance in the plant as they are sufficiently oversized against the requirements. The maintenance performed for cooling towers only when needed. hence most of the time it is breakdown maintenance. There are 16 cooling towers across the plant as enlisted in Table 2.2.1 There are direct / dirty cooling towers which are subjected to process vapours which are corrosive and also affecting the cooling tower structure. further, from operation reliability, thermal performance of cooling tower also need to be analyzed for corrections. Refer table 2.2.2 for performance of cooling towers. CPP cooling tower performance is analyzed for reliability improvement and Alcohol cooling tower structure found critical for corrections on a priority basis to avoid failure / stoppage of cooling tower that will lead to stoppage of alcohol plant
Table 2.2.1: Cooling Tower details at Taloja
Cooling Tower for | Location | Tag No | Make | Type | Capacity
[5 empty] | Circulation | Thermal
[5 empty] | m3/hr | TR
DFA indirect cooling tower - 1 | 7th Floor |  | Paharpur | Natural Draft | 270 | 535.7143
DFA indirect cooling tower - 2 | 7th Floor |  | Paharpur | Natural Draft | 270 | 535.7143
C501/502 dirty cooling tower - 1 | 7th Floor |  | Paharpur | Natural Draft | 200 | 396.8254
Juatasama cooling tower - 1 | 10th Floor | CT 9501A | ARMEC | Forced draft | 350 | 462.963
Juatasama cooling tower - 2 | 10th Floor | CT-9501B | ARMEC | Forced draft | 350 | 462.963
Postcon cooling tower - 1 | Terrace |  | Paharpur | Forced draft | 300 | 396.8254
Paharpur cooling tower-Precon, GDP, Old SPD - 1 | Terrace |  | Paharpur | Forced draft | 650 | 859.7884
Paharpur cooling tower near DM plant-FAP - 1 | Terrace |  | Paharpur | Forced draft | 1400 | 1851.8519
CPP cooling tower - 1 | Terrace |  | Himgiri | Forced draft | 320 | 677.2487
CPP cooling tower - 2 | Terrace |  | Himgiri | Forced draft | 320 | 677.2487
Flaker cooling tower - 1 | Terrace |  | Canara | Forced draft | 100 | 132.2751
C 303 - direct cooling tower - 1 | 10th Floor | CT-9503 | ARMEC | Natural Draft | 220 | 436.5079
CSL DCA Building - 1 | Terrace |  | Canara | Natural Draft | 200 | 396.8254
Glycerin dehydration Plant CT - 1 | Terrace | CT-9504 | ARMEC | Natural Draft | 75 | 148.8095
GDP Plant CT - 1 | Terrace |  | Newtech | Natural Draft | 40 | 79.3651
Table 2.2.2: Cooling Tower Performance details at Taloja
Cooling Tower for | Capacity |  | CW Temperature |  | WBT | Range | Approach | Efficiency
| Circulation | Thermal | Inlet | Outlet
| m3/hr | TR | oC | oC | oC | oC | oC | %
DFA indirect cooling tower - 1 | 454.2789 | 345.5163 | 34.4 | 32.1 | 21 | 2.3 | 11.1 | 17.1642
DFA indirect cooling tower - 2
C501/502 dirty cooling tower - 1
Juatasama cooling tower - 1 | 389.3819 | 154.5166 | 30 | 28.8 | 21 | 1.2 | 7.8 | 13.3333
Juatasama cooling tower - 2 | [5 empty] | 0 | 0
Postcon cooling tower - 1 | Off
Paharpur cooling tower-Precon, GDP, Old SPD - 1
Paharpur cooling tower near DM plant-FAP - 1 | 723.7 | 957.2751 | 27 | 23 | 19 | 4 | 4 | 50
CPP cooling tower - 1 | 446.9923 | 1625.9642 | 39 | 28 | 17 | 11 | 11 | 50
CPP cooling tower - 2
Flaker cooling tower - 1
C 303 - direct cooling tower - 1
CSL DCA Building - 1
Glycerin dehydration Plant CT - 1
GDP Plant CT - 1
3. Pumps, Fans & Rotating machineries: The rotary equipment considered are compressors, turbine, pumps, fans & some special purpose machines. The fatty acid and fatty Alcohol plants are having a major population of pumps. Maintenance team has analyzed the pump failure for last 4 years and improved the performance. however, there are still repetitive failures of pumps which are mainly for mechanical seal failure and bearing failures. The analysis summary along with PI chart is depicted below. The summary extraction is 1. In fatty alcohol plant, 51% of pump failure is due to mechanical seal failure and 40% of pump failures are due to bearing failures. 2. In fatty acid plant, 71% of pump failure is due to mechanical seal failure and 20% of pump failures are due to bearing failures. The root cause analysis for above failures will have followings as root cause of failure 1. Coupling misalignment 2. Loosening of foundation bolts 3. Bearing failure which led to seal failure 4. Cavitation due to starving suction 5. Pump operating at low flow or low head 6. Operation error
Fatty Alcohol Plant Pump Failure Analysis
| SR. NO. | TAG NO | FY 15-16 | FY 14-15 | TOTAL
| 1 | 01G1 B | 5 | 5 | 10
| 2 | 14G02 A | 4 | 3 | 7
| 3 | 01G2 B | 5 | 1 | 6
| 4 | 01G4 A | 4 | 2 | 6
| 5 | 05G9 F | 4 | 2 | 6
| 6 | 01G4 B | 3 | 2 | 5
| 7 | 02G7 A | 3 | 2 | 5
| 8 | 03G6 A | 2 | 3 | 5
| 9 | 01G15 A | 4 | 0 | 4
| 10 | 08G24 | 3 | 1 | 4
| 11 | 01G13 A | 2 | 2 | 4
| 12 | 03G15 B | 2 | 2 | 4
| 13 | 03G17 B | 1 | 3 | 4
Fatty Acid Plant Pump Failure Analysis
| SR. NO. | TAG NO | FY 15-16 | FY 14-15 | TOTAL
| 1 | P-32 A | 12 | 8 | 20
| 2 | P-32 B | 7 | 11 | 18
| 3 | P-518 C | 10 | 5 | 15
| 4 | P-765 | 8 | 6 | 14
| 5 | P-322 B | 11 | 2 | 13
| 6 | P-30 A | 9 | 4 | 13
| 7 | P-322 A | 12 | 0 | 12
| 8 | P-424 B | 7 | 3 | 10
| 9 | P-705 B | 5 | 5 | 10
| 10 | P-4 B | 5 | 5 | 10
| 11 | P-310 B | 5 | 5 | 10
| 12 | P-7120 | 5 | 5 | 10
| 13 | P-512 A | 7 | 2 | 9
| 14 | P-36 A | 6 | 3 | 9
| 15 | P-423 D | 5 | 4 | 9
| 16 | P-705 A | 6 | 2 | 8
| 17 | P-208 A | 4 | 4 | 8
| 18 | P-801 A | 4 | 4 | 8
| 19 | P-514 A | 3 | 5 | 8
| 20 | P-512 B | 5 | 2 | 7
| 21 | P-424 A | 2 | 5 | 7
| 22 | P-820 | 6 | 1 | 7
| 23 | P-4 A | 5 | 2 | 7
| 24 | P-412 B | 5 | 2 | 7
| 25 | P-14 A | 4 | 3 | 7
| 26 | VP-601 B | 2 | 5 | 7
On the similar ground, critical fans and pumps are identified for improving the reliability of operation & maintenance. These are like ID & FD fans of coal heaters which do not have stand by and failure leads to stoppage of the thermic fluid heater. Further, the gas turbine and hydrogen compressors are already equipped with condition monitoring mechanism and are saved from the major breakdowns.
4. Critical Equipment Foundation and Plant structure: Failure analysis of the equipment having drive motor above 50 HP has indicated concerns over the foundation strength and grouting issues. The list is provided in the table below. Plant structure status is reviewed and found corroded at number of places. It is decided to propose repairs and painting of structure & equipment. These are DFA back side pipe racks & equipment structure, TP45 chimney, Hydrogen stack at Linde plant, CPP HRSG chimney, weigh bridge no 1 & TF storage tank in front of pastillator. Identified area of bitumen road which falls under repairs every year to be considered for conversion to RCC
Pump foundations identified for repairs
| Tag No | Model | Sr.no. | location | Q (m3/hr)
| 01G4 A | 2K 6x4-13 A | 20495 | FAP | 154.44
| 01G4 B | 2K 6x4-13 A | 20496 | FAP | 154.44
| 01G1 A | CPK EYM 125-200 | 352444 | FAP | 140
| 01G1 B | CPK EYM 125-250 | 352437 | FAP | 140
| P-308 A | CPK-C-125-315 | 550541 | DFA | 170
| P-308 B | CPK-C-125-315 | 550542 | DFA | 170
3. Conduct sessions on reliability improvements - Identify vendors - Conduct demos for condition monitoring
Cooling Tower: M/s Msquare Engineers delivered a session on reliability of cooling towers operation and maintenance on 26.07.2017. The session created awareness on cooling tower mechanical and thermal performance across the participants. In house team started working on cooling tower structure health assessment and thermal performance evaluation. As a result followings are taken up for reliability improvements of cooling towers. 1. The CPP cooling tower performance studied jointly with Msquare engineers. Based on recommendations the immediate action was to replace the PVC fills and for maintaining the performance reliability, it is recommended to replace the PVC fills once in 4 months. An alternative is also worked out to convert this cooling tower to cross counter flow type cooling tower with perforated PVC splash bars and at least 10% higher capacity to take care of ambient changes as this cooling tower is subjected to constant thermal load irrespective to the seasons and we need the reliable and consistent performance for refrigeration system. 2. The other cooling tower performance were measured and cooling tower structure was studied for assessment of balance life. The structure of the alcohol cooling tower was found having risk of collapse and hence, in a planned shutdown of April 2017, it is taken up for replacement of structure. This will also improve the performance of cooling tower. The structure selected for this cooling tower is Pultruded FRP which has strength equivalent to carbon steel structure or more and is always better than that of wood. Further, the dirty cooling towers - 3 nos - of alcohol plant structure base are found unsafe and hence, decided to replace the same
Centrifugal Pumps: M/s KSB Pumps delivered a session on reliability of cooling towers operation and maintenance on 22.08.2017. The session created awareness on centrifugal pump mechanical and volume performance across the participants. In house team started working on centrifugal pumps failure analysis based on learning from the session. The population of centrifugal pumps being the most in the plant, vendors for online condition monitoring were approached and different concepts were studied which can help us predicting the failure of bearing or seal of the pump. M/s CNJINSTRUMENTS offered ARTESIS Condition Monitoring system. This is a programmed device that is connected to the pump panel and it is monitoring the current variations of motor which is coupled to driven equipment. For first 10 days, the device is capturing the data and log them as a reference. The device then continuously identifies existing and developing faults on electric motors and their driven equipment. MCM utilizes an intelligent, model-based approach to provide anomaly detection by measuring the current and voltage signals from the electrical supply to the motor. It is permanently mounted, generally in the motor control center and is applicable to 3-phase AC fixed and variable speed motors. Accompanying MCMScada Software or Artesis Enterprise Server (OPC Server) is used to view the data. M/s Unilever has installed such 8 units at one of their overseas units which is verified and found performing to client's satisfaction. At Taloja, one trial demo was conducted on 16.01.2017. It is recommended to install three units for coal fired TF heaters ID fans (2 nos) which are critical equipment and Loop reactor Pump.
M/s IFM offered Vibrations sensors and online Monitoring system. The vibration monitor detects the vibration in the system (measured / evaluated physical unit = vibration velocity). This is converted into an analogue signal at the current output. The switching output behavior is determined using the two setting rings. Effective value of the switching threshold, defining the limit value of the vibration velocity. M/s SKF offered system similar to M/s IFM. A vibrations sensor with online monitoring system. Both above systems are studied and decision is made to install vibration sensors for two identified motors along with the on line monitoring. The switching threshold is defined based on the ISO values for the application considered.
M/s Star Glazers called for discussions on reliability. They delivered a session on 01.10.2016 for plant operation & maintenance reliability covering all possible aspects that leads to reliability improvement for a plant. That also conducted a walk in reliability study for one of the sections of fatty Acid plant. They submitted report as well as a proposal for reliability study and training on reliability. The same was reviewed and decided to hold as the cost involve was high and management is inclined to perform the reliability drive in-house. The Moisture remover and an oil filter offered by this vendor are useful from prevention of bearing failures for pumps. It is recommended to install two sets for identified pumps and a proposal will be made as an outcome of this project.
Based on the above studies, the Capex proposals will be generated for next financial year. This will be the starting point for building experience on use of online condition monitoring system. That will decide further and future way forward on Reliability Centered Maintenance. Below are the examples under considerations along with cost benefit analysis.
Cost Benefit Analysis for ARTESIS Instrument Installation
Parameter | Unit | Coal TF heater |  | Hydrogenation
|  | ID fan | FD Fan | LR Pump 705A
Operating Hrs/day | Hrs | 24 | 24 | 18
Having Stand By Unit | Y/N | N | N | N
Number of failures in Yr 2016 | Nos | 1 | 1 | 1
Down time in Year 2016 | Hrs | 28 | 32 | 62
Maintenance cost | Rs. Lakh | 0.45 | 0.45 | 0.23
During down time TF heating changed over from Coal to NG
Loss for fuel changeover | Rs. Lakh /month | 62.5 | 62.5 | 0
| Rs. Lakh/hr | 0.086806 | 0.086806 | 0
| Rs. Lakh | 2.4306 | 2.7778 | 0
Loss due to process undergoes circulation | Rs. Lakh | 2.63 | 7.7 | 0
Throughput opportunity loss | Rs. Lakh | 0 | 0 | 6.81
Total Loss | Rs. Lakh | 5.0606 | 10.4778 | 6.81
Benefits with respect to schemes |  | Benefits of condition monitoring with ARTESIS Instrument
Down time will reduce by 25% | Hrs | 7 | 8 | 15.5
Reduction in maintenance cost by 50% | Rs. Lakh | 0.225 | 0.225 | 0.115
Savings on Loss of fuel Changeover | Rs. Lakh | 0.60764 | 0.69444 | 0
Savings on Loss due to process undergoes circulation | Rs. Lakh | 2.63 | 7.7 | 0
Savings on Throuput opportunity Loss | Rs. Lakh | 0 | 0 | 3.405
Energy savings on account of VFD | Rs. Lakh | 0 | 0 | 0
Total Benefits | Rs. Lakh/annum | 3.4626 | 8.6194 | 3.52
Cost Benefit Analysis using VFD +control valve and Vibration monitoring device
Parameter | Unit | DFA Circulation Pump
|  | P 515 | P 423 | P 308 | P 30
Operating Hrs/day | Hrs | 24 | 24 | 24 | 24
Having Stand By Unit | Y/N | Y | Y | Y | Y
Number of failures in Yr 2016 | Nos
Down time in Year 2016 | Hrs | 193 | 179 | 56 | 176
Maintenance cost | Rs. Lakh | 3.3 | 2.87 | 3.1 | 4.5
During down time TF heating changed over from Coal to NG |  | Since there is a stand by unit, the production loss is negligible as the changeover is done on time.
Loss for fuel changeover | Rs. Lakh /month
Rs. Lakh/hr
Rs. Lakh
Loss due to process undergoes circulation | Rs. Lakh
Throughput opportunity loss | Rs. Lakh
Total Loss | Rs. Lakh | 3.3 | 2.87 | 3.1 | 4.5
Benefits with respect to schemes |  | Benefits of VFD + Control valve |  | Benefits of sensor based Monitoring system
Down time will reduce by 25% | Hrs | 48.25 | 44.75 | 14 | 44
Reduction in maintenance cost by 50% | Rs. Lakh | 1.65 | 1.435 | 1.55 | 2.25
Savings on Loss of fuel Changeover | Rs. Lakh | 0 | 0 | 0 | 0
Savings on Loss due to process undergoes circulation | Rs. Lakh | 0 | 0 | 0 | 0
Savings on Throuput opportunity Loss | Rs. Lakh
Energy savings on account of VFD | Rs. Lakh | 1.48 | 2.4 | 0 | 0
Total Benefits | Rs. Lakh/annum | 3.13 | 3.835 | 1.55 | 2.25
Further, the reliability improvement is also extended to Baddi by including the Fatty acid Plant heat exchangers as a part of universal heat exchangers. Also a separate study was carried out on improving the reliability of baddi DCS operation and a separate report was prepared. At Sewari, while working on the Bitumen storage project, due considerations is given to operational and maintenance reliability while selecting the equipment & laying down the SOP for operations of the system. training provided to operating team on system & instruments operation. Detailed study undertaken for improving operational efficiency and reliability of Boiler at Sewari.
Note on B43: Ajay Kumbhar: VVF WANT TO REPLACED THIS COMPABLOC WITH SPIRAL
Note on C119: Amey Deshpande: P-903 C is running others are off
Note on E119: Amey Deshpande: reading taken on 25 Jan 2017
Note on C122: Amey Deshpande: P-362C is running others are off
Note on E122: Amey Deshpande: reading taken on 25 Jan 2017
Note on E126: Amey Deshpande: reading taken on 18 Jan 2017
Note on E127: Amey Deshpande: reading taken on 12 Jan 2017