## Savings with Proposed Project
Energy Conservations Initiatives towards reduction of Product Conversion Cost
Sl. No. | Area / Location &Sub Headings | Details of action taken | Date of Implementation | Potential Savings / Year in Rs. Lac | Remarks
Lighting Optimization in different area
1 | Sigma Mixer Area | Replacement of CFL light fixtures with LED ligh fixtures: Total 38 Lights are replaced |  | 0.8208 | kwh*24 hrs*30 days*No. of Months*unit rate
2 | Micro Lab & Powder plant | Replacement of CFL light fixtures with LED ligh fixtures Total 72 Lights are replaced |  | 1.242 | kwh*24 hrs*30 days*No. of Months*unit rate
3 | TLP,MSP,RM/PM and Noodles | Idle disconnection and Timer based operation and replacement of some of the lights with LED lights in different areas. Savings of 25KWH |  | 6.75 | kwh*24 hrs*30 days*No. of Months*unit rate
Pumping Energy & Steam savings Optimization
4 | Sigma Mixer Area | Installtion of air washer & Exhaust unit instead of DX coil based AHU only by agreement of J&J technically to meet the requirement. |  | 7.245 | kwh*24 hrs*30 days*No. of Months*unit rate
5 | Optimization of Acma 711 Machine | Replaced the 3HP motor with 1.5HP only done in one Acma.Savings of 1.1KWH |  | 0.049698 | KWH*hrs*days*no of months*unit rate
6 | MSP- H-8 Line | Optimization of H-8 Simplex through VFD- Savings of 15KWH |  | 8.1 | KWH*hrs*days*no of months*unit rate
7 | Noodles Mazzoni plant water Jet Injector- Actual Steam savings | Water jet injector is commissioined and savings are calculated for this FY |  | 26.6066 | Saved steam in KG*av. Production*No. of Months*av. Steam cost per kg (Working sheet attached)
8 | Noodles Mazzoni plant 20HP Vacuum Pump | During opertaion of Mazzoni plant, 20HP vacuum pump is stopped due to water jet injector |  | 4.482 | kwh*av. R hr of plant per month*No. of Months*unit rate
9 | Noodles Root Blower | Replacement of existing 100HP motor with 60HP motor. Savings of 21A or 13.5KWH.Ywearly savings are calculated @ 16Hrs of root blower operation |  | 4.86 | KWH*hrs*days*no of months*unit rate
10 | Utilities | Stopping of Water chillers during Winters |  | 13.234 | units saved per month*no of months*unit rate
11 | Utilities | Optimization of Chiller water cooling tower pumping system during winters and partially stopage of soap lines |  | 3.6 | KWH*hrs*days*no of months*unit rate
12 | Utilities | Optimization of Chilled water secandary/process Pump |  | 4.05 | KWH*hrs*days*no of months*unit rate
13 | MP Boiler | Optimization in MP steam boiler by running only one bed as per the steam requirement.Resulting stopping of one FD Fan and one screw feeder. We have started this practice w.e.f 8th Sep-16. Savings are 1000 Units per day. Taking 8 months single bed operation |  | 4.9219 | units saved/day*no. of days*no. Of month*unit rate
14 | MP Boiler | Both FD fans are having capacity of 40HP and 60HP. Optimized both FD fans through VFD operation and run both FD fans @28Hz . Savings of 20KWH |  | 10.8
15 | Boiler Condensate Recovery | in This Year 42105MT steam is generated and 19784 MT condensate is recovered.46.98% |  | 11.6429 | Condensate Recovery in Mt*cost of RO water
16 | Installation of reinjection fuel system in MP,HP and Thermic Fluid heater | Pet coke handeling Contractor Man Power reduction resulting saving of Rs. 28811 per month. |  | 3.4573 | Saved Rs*no of month
17 | Optimization of bore well operation | Earlier the running hrs were 22 Hrs but by increasing the pipe size the bore well operation is reduced to 12 Hrs. Savings of 20 KWH |  | 4.5 | KWH*hrs*days*no of months*unit rate
18 | DFA Precon & Post Con Vacuum Pump | Capacity reduced from 15HP/220cmh to 165cmh/7.5HP. Savings of 5 KWH |  | 2.7 | KWH*hrs*days*no of months*unit rate
DG set Diesel Savings and Savings due to improved power factor
19 | DG operation reduction due to changing of substation from Katha to Bhatoliklan by follow ups. Savings in FY-16-17 in Lacs | Power failure has been reduce drastically resulting savings in Diesel cost (Compared with (April-15 to June-15) Diesel Consumption |  | 55.11 | Working sheet attached
20 | Power factor | Power factor is maintained between 0.997 to 0.999 wheras incoming power factor remains 0.9 max. calculations are based on 0.9 power factor.In which 1454134 units are saved in this FY |  | 83.6127 | Total units saved*HPSEB unit rate
Energy conservation through Interlocking and Automations
21 | Soap Plant | Improvement of quality of Product along with cost savings by putting auto cleaning of Slip rings of Pouching Machines | 20.06.2015 | 13 | Savings of 13 to 14 lakhs
22 | Automation of TRM with simplex & Duplex plodder Hopper level | Earlier TRM keeps on running 24 Hrs.Now the automation has been done for 7 lines.TRM stopes and starts as per requirement of material in duplex plodder. Savings of 45KWH (Machine Idle Time per day=6 Hrs) |  | 6.075 | KWH*hrs*days*no of months*unit rate
Sr. No. | Area / Location | Data for Assurance |  | Potential Savings/Year in Rs. Lac | Investment in Lac | Payback in Months
1 | Optimization of Noodles plant conveying blower through VFD | Trial taken and savings potential is 14 KWH |  | 5.2416 | 2.5 | 5.7234
2 | Optimization of Precon Hot well pump through VFD | Trial taken and savings potential is 20KWH |  | 11.232 | 3.17 | 3.3868
3 | Replacement of CFL & Tube rods lighting in the entire plant with LED lights | saving potential is 36KWH |  | 20.2176 | 15 | 7.5
4 | Replacement of other lighting like Street,Well glass etc in the entire plant with LED lights | saving potential is 44KWH |  | 12.34 | 12.25 | 12
5 | Water jet reinjection system for MIL | Proven technology as done in Mazzoni |  | 20.76 | 12.81 | 6
6 | Acma Main motor replacement | Trail is successful. 3HP motor is to be replaced with 1.5HP for 6nos of machines. Savings of 1.1KWH in one machine |  | 3.7066 | 0.6 | 2

## Power factor Savings
Month wise saving by Maintaining power factor in FY-2016-17
Month | Overall power factor maintaining in lagging | KWH units Consumed | KVAH Units consumed at maintained power factor | Incoming HPSEB Power factor recorded in Lagging | KVAH Units calculated at incoming power factor | KVAH units saved | Saving in Rs. Per Month in Electricity Bill
2016-04-01 | 0.99663 | 1278880 | 1283200 | 0.9 | 1420977.7778 | 137777.7778 | 771555.5556
2016-05-01 | 0.99474 | 1195360 | 1201680 | 0.9 | 1328177.7778 | 126497.7778 | 715977.4222
2016-06-01 | 0.9961 | 1287600 | 1292640 | 0.9 | 1430666.6667 | 138026.6667 | 770188.8
2016-07-01 | 0.9958 | 1195640 | 1200680 | 0.9 | 1328488.8889 | 127808.8889 | 736179.2
2016-08-01 | 0.99821 | 1161400 | 1163480 | 0.9 | 1290444.4444 | 126964.4444 | 723697.3333
2016-09-01 | 0.99912 | 1088080 | 1089040 | 0.9 | 1208977.7778 | 119937.7778 | 696838.4889
2016-10-01 | 0.99792 | 1057680 | 1059880 | 0.9 | 1175200 | 115320 | 673468.8
2016-11-01 | 0.99784 | 943520 | 945560 | 0.9 | 1048355.5556 | 102795.5556 | 609577.6444
2016-12-01 | 0.99908 | 1040320 | 1041280 | 0.9 | 1155911.1111 | 114631.1111 | 667153.0667
2017-01-01 | 0.99817 | 872760 | 874360 | 0.9 | 969733.3333 | 95373.3333 | 584638.5333
2017-02-01 | 0.99809 | 1170560 | 1172800 | 0.9 | 1300622.2222 | 127822.2222 | 734977.7778
2017-03-01 | 0.99758 | 1155720 | 1158520 | 0.9 | 1284133.3333 | 125613.3333 | 723532.8
Total savings by maintaining Power factor near to unity in FY-2016-17 in Rs. Lac | [6 empty] | 84.0779

## HSD savings
Comparison of Power failure and HSD consumption after power connectivity from Bhatoliklan 66/11KV substation
FY-2014-15 | [5 empty] | FY-2016-17
Month | No of Fails | Fail Time in Minutes | HSD Consumption in Ltr | DG running Hrs | Month | No of Power Fails | Power Fail Time in Minutes | HSD Consumption | DG running Hrs
2014-04-01 | 19 | 1165 | 14846 | 140 | 2016-04-01 | 11 | 790 | 7648 | 69
2014-05-01 | 28 | 835 | 27276 | 169 | 2016-05-01 | 9 | 1140 | 6944 | 64
2014-06-01 | 38 | 2250 | 34968 | 268 | 2016-06-01 | 15 | 788 | 12407 | 114
2014-07-01 | 36 | 1590 | 32930 | 212 | 2016-07-01 | 16 | 443 | 9008 | 81
2014-08-01 | 47 | 2330 | 38052 | 290.5 | 2016-08-01 | 25 | 1630 | 20517 | 185
2014-09-01 | 27 | 3335 | 40989 | 252 | 2016-09-01 | 5 | 71 | 2685 | 28
2014-10-01 | 14 | 1010 | 6169 | 68 | 2016-10-01 | 2 | 470 | 3612 | 35
2014-11-01 | 11 | 895 | 13132 | 124 | 2016-11-01 | 4 | 27 | 1900 | 19
2014-12-01 | 22 | 1775 | 17657 | 166.5 | 2016-12-01 | 8 | 280 | 3263 | 35
2015-01-01 | 17 | 1235 | 26569 | 143 | 2017-01-01 | 25 | 922 | 10845 | 93
2015-02-01 | 16 | 565 | 25212 | 102 | 2017-02-01 | 7 | 86 | 3207 | 31
April-14 to Nov-14 | 220 | 13410 | 208362 | 1523.5 | April-16 to Nov-16 | 127 | 6647 | 82036 | 754
Note: Power supply connected from Bhatoliklan Substation on 28th June-2015, Comparison is of FY-2014-15 and FY 2016-17
No of Power Failure reduced by 42%
HSD consumption reduced by approx.60% or 126326 Ltrs in FY 2016-17
Average HSD price in FY-2016-17= Rs. 43.63/Ltr
Savings in Rs= 126326x43.63= 55.11 Lakhs

## Net savings
Energy Conservations Initiatives towards reduction of Product Conversion Cost
Sl. No. | Area / Location &Sub Headings | Details of action taken | Date of Implementation | Potential Savings / Year in Rs. Lac | Remarks
Lighting Optimization in different area
1 | Sigma Mixer Area | Replacement of CFL light fixtures with LED ligh fixtures: Total 38 Lights are replaced |  | 0.8208 | kwh*24 hrs*30 days*No. of Months*unit rate
2 | Micro Lab & Powder plant | Replacement of CFL light fixtures with LED ligh fixtures Total 72 Lights are replaced |  | 1.242 | kwh*24 hrs*30 days*No. of Months*unit rate
3 | TLP,MSP,RM/PM and Noodles | Idle disconnection and Timer based operation and replacement of some of the lights with LED lights in different areas. Savings of 25KWH |  | 6.75 | kwh*24 hrs*30 days*No. of Months*unit rate
Pumping Energy & Steam savings Optimization
4 | Sigma Mixer Area | Installtion of air washer & Exhaust unit instead of DX coil based AHU only by agreement of J&J technically to meet the requirement. |  | 7.245 | kwh*24 hrs*30 days*No. of Months*unit rate
5 | Optimization of Acma 711 Machine | Replaced the 3HP motor with 1.5HP only done in one Acma.Savings of 1.1KWH |  | 0.049698 | KWH*hrs*days*no of months*unit rate
6 | MSP- H-8 Line | Optimization of H-8 Simplex through VFD- Savings of 15KWH |  | 8.1 | KWH*hrs*days*no of months*unit rate
7 | Noodles Mazzoni plant water Jet Injector- Actual Steam savings | Water jet injector is commissioined and savings are calculated for this FY |  | 26.6066 | Saved steam in KG*av. Production*No. of Months*av. Steam cost per kg (Working sheet attached)
8 | Noodles Mazzoni plant 20HP Vacuum Pump | During opertaion of Mazzoni plant, 20HP vacuum pump is stopped due to water jet injector |  | 4.482 | kwh*av. R hr of plant per month*No. of Months*unit rate
9 | Noodles Root Blower | Replacement of existing 100HP motor with 60HP motor. Savings of 21A or 13.5KWH.Ywearly savings are calculated @ 16Hrs of root blower operation |  | 4.86 | KWH*hrs*days*no of months*unit rate
10 | Utilities | Stopping of Water chillers during Winters |  | 13.234 | units saved per month*no of months*unit rate
11 | Utilities | Optimization of Chiller water cooling tower pumping system during winters and partially stopage of soap lines |  | 3.6 | KWH*hrs*days*no of months*unit rate
12 | Utilities | Optimization of Chilled water secandary/process Pump |  | 4.05 | KWH*hrs*days*no of months*unit rate
13 | MP Boiler | Optimization in MP steam boiler by running only one bed as per the steam requirement.Resulting stopping of one FD Fan and one screw feeder. We have started this practice w.e.f 8th Sep-16. Savings are 1000 Units per day. Taking 8 months single bed operation |  | 4.9219 | units saved/day*no. of days*no. Of month*unit rate
14 | MP Boiler | Both FD fans are having capacity of 40HP and 60HP. Optimized both FD fans through VFD operation and run both FD fans @28Hz . Savings of 20KWH |  | 10.8
15 | Boiler Condensate Recovery | in This Year 42105MT steam is generated and 19784 MT condensate is recovered.46.98% |  | 11.6429 | Condensate Recovery in Mt*cost of RO water
16 | Installation of reinjection fuel system in MP,HP and Thermic Fluid heater | Pet coke handeling Contractor Man Power reduction resulting saving of Rs. 28811 per month. |  | 3.4573 | Saved Rs*no of month
17 | Optimization of bore well operation | Earlier the running hrs were 22 Hrs but by increasing the pipe size the bore well operation is reduced to 12 Hrs. Savings of 20 KWH |  | 4.5 | KWH*hrs*days*no of months*unit rate
18 | DFA Precon & Post Con Vacuum Pump | Capacity reduced from 15HP/220cmh to 165cmh/7.5HP. Savings of 5 KWH |  | 2.7 | KWH*hrs*days*no of months*unit rate
DG set Diesel Savings and Savings due to improved power factor
19 | DG operation reduction due to changing of substation from Katha to Bhatoliklan by follow ups. Savings in FY-16-17 in Lacs | Power failure has been reduce drastically resulting savings in Diesel cost (Compared with (April-15 to June-15) Diesel Consumption |  | 55.11 | Working sheet attached
20 | Power factor | Power factor is maintained between 0.997 to 0.999 wheras incoming power factor remains 0.9 max. calculations are based on 0.9 power factor.In which 1454134 units are saved in this FY |  | 83.6127 | Total units saved*HPSEB unit rate
Energy conservation through Interlocking and Automations
21 | Soap Plant | Improvement of quality of Product along with cost savings by putting auto cleaning of Slip rings of Pouching Machines | 20.06.2015 | 13 | Savings of 13 to 14 lakhs
22 | Automation of TRM with simplex & Duplex plodder Hopper level | Earlier TRM keeps on running 24 Hrs.Now the automation has been done for 7 lines.TRM stopes and starts as per requirement of material in duplex plodder. Savings of 45KWH (Machine Idle Time per day=6 Hrs) |  | 6.075 | KWH*hrs*days*no of months*unit rate
Total Savings in Rs. lac |  |  |  | 276.8598