## till Mar-2015 (hidden)
Month | Equipment | Planned | Completed | Slippage |  | Condition Monitoring of Bearing |  | Month | Equipment | Equipment Covered
2014-04-14 | Motor | 114 | 114 | 0 | 2015-09-14 | Bearing Replacement | 12
| Panel | 25 | 25 | 0 | 2015-04-14 | Bearing Replacement | 17
2014-05-14 | Motor | 118 | 118 | 0 | 2014-05-14 | Bearing Cm | 30 | 2014-05-14 | Thermography | 91
| Panel | 36 | 36 | 0 |  | Bearing Replacement | 5 |  | Greasing | 43
2014-06-14 | Motor | 119 | 119 | 0 |  | Planned for bearing replacement | 3 | 2014-06-14 | Thermography | NA
| Panel | 40 | 40 | 0 |  | Motor burnt | 2 |  | Greasing | 7
2014-07-14 | Motor | 118 | 112 | 6 | 2014-06-14 | Bearing Cm | 102 | 2014-07-14 | Thermography | NA
| Panel | 40 | 40 | 0 |  | Bearing Replacement | 9 |  | Greasing | 36
2014-08-14 | Motor | 117 | 115 | 2 |  | Planned for bearing replacement | 4 | 2014-07-14 | Thermography | NA
| Panel | 40 | 40 | 0 |  | Motor burnt | 1 |  | Greasing | 21
2014-09-14 | Motor | 120 | 120 | 0
| Panel | 38 | 38 | 0
2014-10-14 | Motor | 114 | 112 | 2 | 2014-07-14 | Bearing Cm | 0 | 2014-10-14 | Thermography | NA
| Panel | 25 | 25 | 0 |  | Bearing Replacement | 11 |  | Greasing | 56
2014-11-14 | Motor | 118 | 116 | 2 |  | Planned for bearing replacement | 0 | 2014-11-14 | Thermography | NA
| Panel | 37 | 37 | 0 |  | Motor burnt | 2 |  | Greasing | 13
2014-12-14 | Motor | 121 | 111 | 10 | 2014-08-01 | Bearing Cm | 27 | 2014-12-14 | Thermography | 91
| Panel | 39 | 39 | 0 |  | Bearing Replacement | 3 |  | Greasing | 69
2015-01-14 | Motor | 128 | 128 | 0 |  | Planned for bearing replacement | 0 | 2015-01-14 | Thermography | 0
| Panel | 40 | 40 | 0 |  | Motor burnt | 1 |  | Greasing | 30
2015-02-14 | Motor | 119 | 119 | 0 | 2014-10-14 | Bearing Cm | 30 | 2015-02-14 | Thermography | 0
| Panel | 40 | 40 | 0 |  | Bearing Replacement | 9 |  | Greasing | 0
2015-03-14 | Motor | 122 | 115 | 7 |  | Planned for bearing replacement | 0 | 2015-03-14 | Thermography | 92
| Panel | 38 | 38 | 0 |  | Motor burnt | 1 |  | Greasing | 40
[5 empty] | 2014-11-01 | Bearing Cm | 2
[6 empty] | Bearing Replacement | 7
[6 empty] | Planned for bearing replacement | 0
[6 empty] | Motor burnt | 3
[5 empty] | 2014-12-01 | Bearing Cm | 76
[6 empty] | Bearing Replacement | 6
[6 empty] | Planned for bearing replacement | 2
[6 empty] | Motor burnt | 3
[5 empty] | 2015-01-01 | Bearing Cm | 248
[6 empty] | Bearing Replacement | 11
[6 empty] | Planned for bearing replacement | 0
[6 empty] | Motor burnt | 0
[5 empty] | 2015-02-01 | Bearing Cm | 206
[6 empty] | Bearing Replacement | 16
[6 empty] | Planned for bearing replacement | 2
[6 empty] | Motor burnt | 0
[5 empty] | 2015-03-01 | Bearing Cm | 19
[6 empty] | Bearing Replacement | 4
[6 empty] | Planned for bearing replacement | 1
[6 empty] | Motor burnt | 2
Note on M7: electrical.taloja: Schedule is of 3months next is in Sep-14
Note on M8: electrical.taloja: Grease Gun is having problem
Note on M9: electrical.taloja: Schedule is of 3months next is in Sep-14
Note on M11: electrical.taloja: Schedule is of 3months next is in Sep-14
Note on M15: electrical.taloja: Schedule is of 3months next is in Jan-15
Note on M17: electrical.taloja: Schedule is of 3months next is in Jan-15
Note on M21: admin: Schedule is quarterly next is March-2015
Note on M23: admin: Next schedule is MAR-2015

## till apr-2015 (hidden)
Month | Equipment | Planned | Completed | Slippage | Condition Monitoring of Bearing |  |  | Month | Equipment | Equipment Covered | Month | Equipment | Nos/status
2015-04-14 | Motor | 120 | 111 | 9 | 2015-04-14 | Bearing Cm | 85 | 2015-04-14 | Thermography | 0 | 2015-04-14 | Maintenance free battery | 16
| Panel | 25` | 25 | 0 |  | Bearing Replacement | 4 |  | Greasing | 14 |  | Distilled water battery | 9*2times
2015-05-14 | Motor | 125 | 123 | 2 |  | Planned for bearing replacement | 0 | 2015-05-14 | Thermography | 92(internal) & 62(External) |  | Emergency Light trial | Ok
| Panel | 33 | 33 | 0 |  | Motor burnt | 1 |  | Greasing | 25 | 2015-05-14 | Maintenance free battery | NA
2015-06-14 | Motor | 122 | 119 | 3 | 2015-05-14 | Bearing Cm | 124 | 2015-06-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 37 | 0 | 0 |  | Bearing Replacement | 10 |  | Greasing | 45 |  | Emergency Light trial | Ok
2015-07-14 | Motor | 121 | 121 | 0 |  | Planned for bearing replacement | 0 | 2015-07-14 | Thermography | 0 |  | Transformer PM | 6
| Panel | 40 | 40 | 0 |  | Motor burnt | 1 |  | Greasing | 26 | 2015-06-14 | Maintenance free battery | NA
2015-08-14 | Motor | 119 | 119 | 0 | 2015-06-14 | Bearing Cm | 110 | 2015-08-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 38 | 38 | 0 |  | Bearing Replacement | 7 |  | Greasing | 25 |  | Emergency Light trial | Ok
2015-09-14 | Motor | 121 | 121 | 0 |  | Planned for bearing replacement | 0 | 2015-09-14 | Thermography | 98 | 2015-07-14 | Maintenance free battery | 15
| Panel | 34 | 34 | 0 |  | Motor burnt | 2 |  | Greasing | 43 |  | Distilled water battery | 9*2times
2015-10-14 | Motor | 113 | 112 | 1 | 2015-07-14 | Bearing Cm | 54 | 2015-10-14 | Thermography | 0 |  | Emergency Light trial | Ok
| Panel | 25 | 34 | 0 |  | Bearing Replacement | 11 |  | Greasing | 13 | 2015-08-14 | Maintenance free battery | NA
2015-11-14 | Motor | 120 | 115 | 4 |  | Planned for bearing replacement | 0 | 2015-11-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 34 | 34 | 0 |  | Motor burnt | 1 |  | Greasing | 44 |  | Emergency Light trial | Loop reactor fitting problem rest ok
2015-12-14 | Motor | 127 | 127 | 0 | 2015-08-14 | Bearing Cm | 115 | 2015-12-14 | Thermography | 1 |  | Transformer PM | 7
| Panel | 27 | 27 | 0 |  | Bearing Replacement | 5 |  | Greasing | 59 | 2015-09-14 | Maintenance free battery | NA
2016-01-01 | Motor | 118 | 118 | 0 |  | Planned for bearing replacement | 5 | 2016-01-01 | Thermography | 87 |  | Distilled water battery | 9*2times
| Panel | 31 | 31 | 0 |  | Motor burnt | 0 |  | Greasing | 10 |  | Emergency Light trial | CPP PMCC, Jutasama 3rd floor,Syndet 1st floor problem rest ok
2016-02-02 | Motor | 123 | 122 | 1 | 2015-09-14 | Bearing Cm | 0 | 2016-02-01 | Thermography | 96 |  | Transformer PM | NA
| Panel | 38 | 38 | 0 |  | Bearing Replacement | 5 |  | Greasing | 67 |  | Earthing Pit PM | OK
2016-03-02 | Motor | 123 | 123 | 0 |  | Planned for bearing replacement | 2 |  |  |  | 2015-10-14 | Maintenance free battery | 16
| Panel | 34 | 34 | 0 |  | Motor burnt | 2 |  |  |  |  | Distilled water battery | 9*2times
[5 empty] | 2015-10-14 | Bearing Cm | 123 |  |  |  |  | Emergency Light trial | FAP 2nd floor CFL Fitting N/W rest ok
[6 empty] | Bearing Replacement | 8 |  |  |  |  | Transformer PM | NA
[6 empty] | Planned for bearing replacement | 0 |  |  |  |  | Earthing Pit PM | NA
[6 empty] | Motor burnt | 1 |  |  |  | 2015-11-14 | Maintenance free battery | NA
[5 empty] | 2015-11-14 | Bearing Cm | 0 |  |  |  |  | Distilled water battery | 10*2times
[6 empty] | Bearing Replacement | 8 |  |  |  |  | Emergency Light trial | Ok 24.11.15
[6 empty] | Planned for bearing replacement | 2 |  |  |  |  | Transformer PM | 8
[6 empty] | Motor burnt | 0 |  |  |  |  | Earthing Pit PM | NA
[5 empty] | 2015-12-14 | Bearing Cm | 72 |  |  |  | 2015-12-14 | Maintenance free battery | NA
[6 empty] | Bearing Replacement | 8 |  |  |  |  | Distilled water battery | 9*2times
[6 empty] | Planned for bearing replacement | 0 |  |  |  |  | Emergency Light trial | Ok 27.12.15
[6 empty] | Motor burnt | 0 |  |  |  |  | Transformer PM | NA
[5 empty] | 2015-01-01 | Bearing Cm | 101 |  |  |  |  | Earthing Pit PM | NA
[6 empty] | Bearing Replacement | 6 |  |  |  |  | Fire Alarm | OK
[6 empty] | Planned for bearing replacement | 0 |  |  |  | 2016-01-01 | Maintenance free battery | 15
[6 empty] | Motor burnt | 0 |  |  |  |  | Distilled water battery | 10*2times
[5 empty] | 2015-02-01 | Bearing Cm | 15 |  |  |  |  | Emergency Light trial | Ok 20.1.16
[6 empty] | Bearing Replacement | 14 |  |  |  |  | Transformer PM | NA
[6 empty] | Planned for bearing replacement | 0 |  |  |  |  | Earthing Pit PM | NA
[6 empty] | Motor burnt | 0 |  |  |  | 2016-02-01 | Maintenance free battery | 0
[5 empty] | 2015-03-01 | Bearing Cm | 227 |  |  |  |  | Distilled water battery | 10*2times
[6 empty] | Bearing Replacement | 13 |  |  |  |  | Emergency Light trial | Ok 24.2.16
[6 empty] | Planned for bearing replacement | 2 |  |  |  |  | Transformer PM | Ok 10.2.16
[6 empty] | Motor burnt | 4 |  |  |  |  | Earthing Pit PM | NA
[12 empty] | Capacitor | Ok
[11 empty] | 2016-03-01 | Maintenance free battery | 0
[12 empty] | Distilled water battery | 10*2times
[12 empty] | Emergency Light trial | Ok 30.3.16
[12 empty] | Transformer PM | NA
[12 empty] | Earthing Pit PM | Ok 18.3.16
Note on E5: admin: 01G4B(standby motor under maintenenc); TF4-32C
Note on M5: admin: 92 thermography points coverd internally by sal & External thermography conducted on 29.5.15 by M/S Microaids
Note on E7: admin: P-308A;P-411B;P-422D-change over not given of standby motor
Note on M7: admin: Schedule is in Sept-15
Note on M9: admin: Schedule is in Sept-15
Note on M11: admin: Schedule is in Sept-15
Note on E15: admin: FD-309 motor
Note on E17: Pending motors 03G6A,P-33A,P-202,P-456A
Note on E19: Pending motors 03G6A,P-33A,P-202,P-456A from previous month completed
Note on M19: admin: K3 panel MCCB contact area cleaned and PCC R phase contact cleaned. 9/12/15 by SAL
Note on E23: admin: P-456A pending
Note on I33: admin: 01G17 and C-403
Note on I49: admin: P-705A motor bearing replacement

## Electrical
Month | Equipment | Shutdown | Planned | Completed | Slippage | Condition Monitoring of Bearing |  |  | Month | Equipment | Equipment Covered | Month | Equipment | Nos/status
2016-04-14 | Motor |  | 113 | 112 | 1 | 2016-04-14 | Bearing Cm | 51 | 2016-04-14 | Thermography | 0 | 2016-04-14 | Maintenance free battery | 14
| Panel |  | 25 | 25 | 0 |  | Bearing Replacement | 10 |  | Greasing | 0 |  | Distilled water battery | 9*2times
2016-05-14 | Motor |  | 107 | 107 | 0 |  | Planned for bearing replacement | 0 | 2016-05-14 | Thermography | 1 |  | Emergency Light trial | OK taken on 25.4.16
| Panel |  | 29 | 29 | 0 |  | Motor burnt | 2 |  | Greasing | 0 | 2016-05-14 | Transformer PM | 7 done by AVV on 3.5.16
2016-06-14 | Motor |  | 103 | 97 | 6 | 2016-05-14 | Bearing Cm | 49 | 2016-06-14 | Thermography | 100 |  | Earthing Pit PM | NA
| Panel |  | 29 | 29 | 0 |  | Bearing Replacement | 5 |  | Greasing | 16 |  | Emergency Light trial | 30.5.16
2016-07-14 | Motor |  | 96 | 89 | 7 |  | Planned for bearing replacement | 2 | 2016-07-14 | Thermography |  |  | Distilled water battery | 9*2times
| Panel |  | 25 | 25 | 0 |  | Motor burnt | 2 |  | Greasing |  | 2016-06-14 | Maintenance free battery | NA
2016-08-14 | Motor | 52 | 108 | 107 | 3 | 2016-06-14 | Bearing Cm | 187 | 2016-08-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 0 | 25 | 25 | 0 |  | Bearing Replacement | 5 |  | Greasing | 0 |  | Emergency Light trial | 1.6.16
2016-09-14 | Motor | 10 | 106 | 98 | 8 |  | Planned for bearing replacement | 4 | 2016-09-14 | Thermography | 0 |  | fire alarm testing | 21 & 22.6.16
| Panel | 1 | 24 | 24 | 0 |  | Motor burnt | 0 |  | Greasing | 0 | 2016-07-14 | Maintenance free battery
2016-10-14 | Motor | 6 | 115 | 109 | 6 | 2016-07-14 | Bearing Cm |  | 2016-10-14 | Thermography | 86 |  | Distilled water battery
| Panel | 0 | 24 | 24 | 0 |  | Bearing Replacement |  |  | Greasing | 0 |  | Emergency Light trial
2016-11-14 | Motor | 19 | 113 | 98 | 15 |  | Planned for bearing replacement |  | 2016-11-14 | Thermography | 0 |  | fire alarm testing
| Panel | 3 | 29 | 29 | 0 |  | Motor burnt |  |  | Greasing | 44 | 2016-08-14 | Maintenance free battery | NA
2016-12-14 | Motor | 0 | 123 | 119 | 4 | 2016-08-14 | Bearing Cm | 10 | 2016-12-14 | Thermography | 61 |  | Distilled water battery | 9*2times
| Panel | 0 | 21 | 21 | 0 |  | Bearing Replacement | 7 |  | Greasing | 22 |  | Emergency Light trial | 17.08.2016
2017-01-14 | Motor | 0 | 104 | 104 | 0 |  | Planned for bearing replacement | 0 | 2017-01-14 | Thermography | 19 |  | fire alarm testing | NA
| Panel | 0 | 36 | 36 | 0 |  | Motor burnt | 1 |  | Greasing | 26 | 2016-09-01 | Maintenance free battery | NA
2017-02-14 | Motor | 0 | 96 | 96 | 0 | 2016-09-14 | Bearing Cm | 56 | 2017-02-14 | Thermography | 0 |  | Distilled water battery | 9*2times
| Panel | 0 | 30 | 30 | 0 |  | Bearing Replacement | 8 |  | Greasing | 0 |  | Emergency Light trial | 22.09.16/ 23.09.16
2017-03-14 | Motor | 0 | 97 | 96 | 1 |  | Planned for bearing replacement | 0 | 2017-03-14 | Thermography | 83 |  | fire alarm testing | NA
| Panel | 0 | 29 | 29 | 0 |  | Motor burnt | 1 |  | Greasing | 0 | 2016-10-01 | Maintenance free battery | 15
[6 empty] | 2016-10-14 | Bearing Cm | 4 |  |  |  |  | Distilled water battery | 9*2times
|  |  | 1281 | 1232 | 96.1749 |  | Bearing Replacement | 7 |  |  |  |  | Emergency Light trial | 17.10.16
|  |  | 326 | 326 | 100 |  | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 2 |  |  |  | 2016-11-01 | Maintenance free battery | NA
[6 empty] | 2016-11-14 | Bearing Cm | 140 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 12 |  |  |  |  | Emergency Light trial | -
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 3 |  |  |  | 2016-12-01 | Maintenance free battery | NA
[6 empty] | 2016-12-14 | Bearing Cm | 4 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 6 |  |  |  |  | Emergency Light trial | 01.12.16
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | 12.12.16/ 13.12.16
[7 empty] | Motor burnt | 1 |  |  |  | 2017-01-01 | Maintenance free battery | NA
[6 empty] | 2017-01-14 | Bearing Cm | 218 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 8 |  |  |  |  | Emergency Light trial | 11.01.17
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 1 |  |  |  | 2017-02-01 | Maintenance free battery | NA
[6 empty] | 2017-02-14 | Bearing Cm | 0 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 10 |  |  |  |  | Emergency Light trial | 11.01.17
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 4 |  |  |  | 2017-03-01 | Maintenance free battery | NA
[6 empty] | 2017-03-14 | Bearing Cm | 0 |  |  |  |  | Distilled water battery | 9*2times
[7 empty] | Bearing Replacement | 10 |  |  |  |  | Emergency Light trial | 14.03.17
[7 empty] | Planned for bearing replacement | 0 |  |  |  |  | fire alarm testing | NA
[7 empty] | Motor burnt | 2
| Shutdown Motor |  |  | 22
Note on F2: admin: 03G3A Pending
Note on N4: admin: 02G1 bypass contact cleaned
Note on J9: 20P03B & 02G1
Note on F10: AUG: Pre. Month: VP-351A P-354B P-308A
Note on F12: SEP: P-964,513B,819B, VP-351B, 14B, D-1-2, CT-903B Pre. Month: P-354B
Note on F13: Stability Chamber QC
Note on F14: OCT-16: 01G13A, P-802B, P-364A, P-1013C PRE. MONTH: D-1-2, CTF-903B
Note on F16: 01G16A,P-966, P-202,VPX-601B, CTF-1,P-362C, P-657A, P-9002B, P-808B, P-453B, P-351B, 354A, 355A, 356A,361B
Note on C17: CPP PMCC 11 KV HT Panel 10 MVA, 22 KV HT Panel
Note on F18: P-710B, P-652, P-654, P-655
Note on N18: admin: K3 panel MCCB contact area cleaned and PCC R phase contact cleaned. 9/12/15 by SAL
Note on J21: P-7102
Note on F24: P-513B
Note on J25: P-7100A
Note on J29: P-31B P-1001B
Note on J32: admin: 01G17 and C-403
Note on J33: 06G1A VP-7103B P-7100A
Note on J37: P-7120
Note on J41: Pestillator Forklift Stering Motor
Note on J45: 01G19B P-1016B Degasser Blower ETP Submersible Pump 07G7B
Note on J49: P-3B P-7104B

## Bearing failure (hidden)
Sr.No. | Date | Eqpt.Name | Tag No. | Kw/Rpm | Bearing No. | Reported By | Work Done By | Location
2014-05-13
1 | 06.05.14 | CW supply Pump for Splitting & SW | P-9002A | 90/1400 | 6317/6316 C3 |  | CPP/RANA | CGS
2 | 07.05.14 | Distillate transfer pump | P-514B | 7.5/2900 | 6208ZZC3 |  | GTC | DFA
3 | 13.05.14 | Residue transfer pump-1 | P-407A | 9.3/2940 | 6309C3 |  | CPP
4 | 18.05.14 | Vaccum pump | P-522 | 5.5/1440 | 6308/6208 ZZ | DILIP/AVV
5 | 25.05.14 | K-3 Reboiler circulation pump | P-29B | 15 | 6309C3
2014-06-13
1 | 05.06.14 | Circulation pump for 01D2 | 01G2A | 11/2945' | 6312/6311ZZC3 | SAL | RSM/RNP | FAP
2 | 05.06.14 | Bottom circulation pump | P-511B | 15/1450 | 6309/6209ZZC3 | RNP/DLK | RNP/DLK | DFA
3 | 10.06.14 | Circulation pump for 01D4 | 01G4A | 55/2950 | 6315C3/6215C3 |  | RSM/AVV | FAP
4 | 12.06.14 | Atlas copco air compressor | 06G1D | 75/2975 | NU215ECP/6215K4VT269 |  | DLK/Aircom | Utility
5 | 14.06.14 | Oil fat trap pump | P-816B | 3.7/2900 | 6206ZZC3/6205ZZC3 |  | RSM/AVV | New TF
6 | 20.06.14 | Hotwell Pump | P-206.3/D-1-1 | 30/2940 | 6312zz/6311zz |  | RSG | Noodle plant ,used for D-1-1
7 | 23.06.14 | Hot Well Pump-1 - Loop Reactor | P-802A | 15/2910 | 6209ZZC3 | RSM | RSG | Loop Reactor
8 | 30.06.14 | pump for cooling water return-3 | C-403 | 11/2935' | 6309 ZZc3/6309ZZC3 |  | CPP/SKP | Flaker top
9 | 29.06.14 | Feed Pump Pestillator-1 | P-651A | 15/2940 | 6309C3 |  | AVV/SKP | GDP GR Floor
2014-07-13
1 | 01.07.14 | Tempered water circulation pump | 01G14B | 75/1480 | 6317C3/6316C3 |  | RSM/RANA | Pestillator terrace spare motor for 01G14B
2 | 01.07.14 | Hydrocarbon transfer pump | 01G20 | 3.7/2885 | 6308ZZC3/6307ZZC3 | SKP | Rana/CPP | FAP
3 | 9.7.14 | Linde FD fan | F-102 | 7.5/2885 | 6308ZZC3/6307ZZC3 | CM | SAL | Linde First floor
4 | 11.7.14 | Flaker cooling tower | C-402 | 11/2935 | 6309ZZC3 | AVV | SAL/SKP | Flaker top
5 | 10.07.14 | BFW | 07U1G2B | 7.5/2910 | 7308BE2RS/6206ZZRC3 | CM |  | Old boiler
6 | 16.7.14 | Hotwell Pump | D-1-2 | 30/2930 | 6313C3 | CM | SAL | DFA 3rd floor
7 | 18.7.14 | Linde ID fan | F-101 | 30/2945 | 6312C3/6212C3 | CPP | SAL/RANA | Lind ID Fan
8 | 19.7.14 | CPP CT fan-1 | P-1016A | 15/1450 | 6309C3 | RNP | RNP | CPP Cooling tower CT Fan
9 | 14.07.14 | PITCH PUMP | P-7110B | 3.7 | 6205ZZC3/6206ZZC3 | SKP | SKP/AVV | GDP ground floor
10 | 25.07.14 | Effluent transfer pump | 05U1G8 | 1.5/900 | 62052ZZC3 | RSM/SKP | TOM | Old boiler terrace
11 | 30.7.14 | D-20 DM water V-303 | P-34B | 7.5/2850 | 6308ZZC3/6307ZZC3 | SAL |  | New boiler terrace
2014-08-13
12 | 13.08.14 | TANK FORM FEED PUMP | P-7100A | 9.3/2860 | 6308ZZC3/6307ZZC3 | RSG/RSM |  | New TF
13 | 16.08.14 | Circulation pump for 01D3 | 01G3A | 30/2955 | 6312C3/5212C3 | CPP | RNP/RSM | FAP
14 | 22.08.14 | CPP CT fan-2 | P-1016B | 15/1450 | 6309C3 | CM | RSM/GTC | CPP Cooling tower CT Fan
2014-10-14
1 | 05.10.14 | C401 bottom transfer | P-424B | 7.5/2935 | 6208ZZC3 | RSM/AVV | RSM/CPP | DFA
2 | 08.10.14 | Hotwell pump Sec-3 | 03G18A | 15/2920 | 6209ZZC3 |  | CPP | Alcohol
3 | 09.10.14 | Bioler feed water pump 3TPH | 07U1G2A | 7.5/2910 | 6308ZZC3/6206ZZC3 |  | SAL | Utility
4 | 09.10.14 | Bioler feed water pump 3TPH | 07U1G2B | 7.5/2910 | 6308ZZC3/6206ZZC3 |  | SAL | Utility
5 | 09.10.14 | Froced draft fan bioler 3TPH | 07U1G1B | 11/2910' | 6209ZZC3 |  | RNP | Utility
6 | 07.10.14 | Terpered cooling water III pump | 01G16A | 55/1400 | 6215C3/6315C3 |  | SAL | Alcohol
7 | 20.10.14 | L/E or Refulx pump of C401 | P-421B | 5.5/2932 | 6208ZZC3 | RSG/DLK |  | DFA
8 | 21.10.14 | Oil dhakka circulation pump | P-824 | 22/2930 | 6310C3
9 | 23.10.14 | Inline pump for thermal oil | 03G4A | 11/1450 | 6309ZZC3/6308ZZC3 | CPP | RSG | Alcohol
2014-11-14
1 | 5.11.14 | Air compressor | 06G1G | 75/2430 | NU215ECP/6215K4VT269 | CM | RSM/Airkom vendor | DFA Air compressor house
2 | 7.11.14 | MCT blitcher |  | 3.7 | 6207ZZC3/6208ZZC3 |  | SAL | DFA first floor
3 | 8.11.14 | Thermic [pump | P-7122 | 7.5/1440 | 6308ZZC3/6307ZZC3 | SAL/CPP | AVV/RSM | GDP
4 | 13.11.14 | BFW | 07U1G3B | 7.5/2930 | 6308ZZC3/6206ZZC3 | CM | rsm/sal | Old boiler
5 | 15.11.14 | BFW | 07U1G3A | 7.5/2930 | 6308ZZC3/6206ZZC3 | CM | avvv/rsm | Old boiler
6 | 22.11.14 | Chilling Inlet Motor | P-962 | 18.5/2920 | 6309ZZC3/6209ZZC3 | SKP/RNP | rsm | Pastillator
7 | 24.11.14 | Air compressor | 06G1G | 75/2430 | NU215ECP/6215K4VT269 | avv/skp |  | DFA Air compressor house
2014-12-14
1 | 06.12.14 | CONDENSATE PUMP | 07G7B |  | 6203ZZ | avv/rnp | rnp | Near 7P-45C heater
2 | 14.12.14 | Hot oil circulation pump-1 | P-311A | 15/1475 | 6309C3 | CPP/RNP | RSM/AVV/RANA | DFA
3 | 20.12.14 | Direct cooling water return pump-2 | P-422B | 22/2940 |  | AVV/RSM |  | DFA 2nd Floor
4 | 28.12.14 | HOT WATER PUMP-A | P-1015A | 18.5/2930 | 6309ZZC3/6209ZZC3 | RNP/DLK |  | CPP CT fan
5 | 29.12.14 | Hotwell Pump | P-360A | 30/2830 | 6312ZZC3/6311ZZC3 | rnp/skp | RSG | Jutasama 3rd floor
6 | 31.12.14 | Agitator for 08T9A | 08N14A | 4/1440 | 6205ZZC3/6206ZZC3 | sal | sal | Old TF
7 | 31.13.14 | Agitator for 08T3B | 08N18B | 2.2/1420 | 6205ZZC3/6206ZZC4 | sal | sal | OLD TF
2015-01-14
1 | 7.1.15 | Cooling water pump | 05G9D | 30/2955 | 6312/6212C3 |  | sal/cpp | Old boiler
2 | 9.1.15 | ETP Pit Pump | P-913B | 7.5/2850 | 6308ZZC3/6307ZZC3 | sal |  | Old boiler
3 | 10.1.15 | Feed Pump | P-651A | 15/2940 | 6309C3 | sal | sal | GDU postcon
4 | 12.1.15 | B/P Pump K3' | P-355A | 11/2940 | 6309C3 | sal | sal | Jutasama 1st floor
5 | 13.1.15 | Cooling water pump | 05G9G | 30/2955 | 6312ZZC3 | rnp | sal | Old boiler
6 | 13.1.15 | Dehydrator circulation Pump | P-351B | 22/2944 | 6310C3 | sal | sal | Jutasama 4th floor
7 | 14.1.15 |  | P-7106 | 5.5/2920 | 6208ZZC3 | cpp/skp | sal | GDP gnd floor
8 | 16.1.15 | Feed pump Jutasama | P-104D | 30/2930 | 6312C3/6312C3 | sal | sal | New TF
9 | 21.1.15 | Chilling Inlet Motor | P-962 | 18.5/2920 | 6309ZZC3/6209ZZC3 | gtc | sal | Pastillator
10 | 25.1.15 | Blower | BDG-2 | 0.55/2840 | 6202ZZC3 | cpp/avv |  | Old boiler
11 | 28.1.15 | cooling water pump -1 | C-301 | 11/2935 | 6309ZZC3 | rsg/avv | rnp | Flaker
2015-02-14
1 | 7.02.15 |  | 07U2G1B | 110/1400 | 6319C3/6316C3 | cpp/skp | sal/rnp | TP-45
2 | 8.2.15 |  | P-36B | 22/2940 | 6210C3/6210C3 | avv/skp | cpp/rsm | DFA 2nd Floor
3 | 8.2.15 |  | P-27A | 15/1460 | 6309ZZC3 | avv/skp | cpp/rsg | DFA 6th floor
4 | 7.2.15 |  | 02G8A | 37kw | 6312C3/6212C3 | avv/skp | cpp/rsg | FAP ground floor
5 | 9.2.15 |  | P-30B | 7.5/2900 | 6208ZZC3/6305ZZC3 | avv/skp | rsg/cpp | DFA ground floor
6 | 9.2.15 |  | P-33A | 9.3/1450 | 6309C3/6308C3 | avv/skp | cpp | DFA
7 | 9.2.15 |  | D-1-1 | 30/2940 | 6312ZZC3/6311ZZC3 | gtc | rsm/sal | DFA 3rd floor
8 | 10.2.15 |  | Filter press-A | 1.5/1415 | 6205ZZC3 | avv/dlk | rsm | FAP ground floor
9 | 11.2.15 | Blower | BDG-2 | 0.55/2840 | 6202ZZC3 | gtc | rnp/rsg | Old boiler
10 | 16.2.15 |  | 07U1G1A | 18.5/2910 | 6209C3 | cpp |  | SM-50 blower
11 | 16.2.15 |  | 06G1G exhaust blower motor | 2/920 | 6007ZZ/6007ZZ | airkom rahul | sal | DFA boiler house 75 kw compressor
12 | 14.2.15 |  | P-962 | 18.5/2920 | 6309ZZC3/6209ZZC3 |  | rsm | Pastillator ground floor
13 | 21.2.15 |  | P-318A | 5.5/2880 | 6205ZZC3/6306ZZC3 | sal | rsg/rana | DFA
14 | 25.2.15 |  | 03G1B | 55/2960 | 6315C3/6215C3 | rnp | rnp/rana | FAP 1st floor
15 | 25.2.15 |  | P-7120 | 3.7/2930 | 6306ZZC3/6206ZZC3 | cpp | cpp | GDP
16 | 28.5.15 |  | 05G9E | 30/2955 | 6312C3 |  | rsm/rnp/cpp | Old boiler
2015-03-14
1 | 28.2.15 |  | 02G5AG1 | 0.75/910 | 6205ZZC3 | CM | rsm | FAP
2 | 2.03.2015 |  | P-208A | 7.5/2900 | 6305ZZC3/6208ZZC3 | avv/rsg | avv/cpp | DFA
3 | 3.3.15 |  | TF-4-32B | 3.7/2865 | 6206ZZC3/6205ZZC3 | rsm |  | Flaker backside
4 | 26.3.15 |  | 03G3A | 37/2955 | 6312C3/6313C3 | rsm | sal | FAP ground floor
2015-04-14
1 | 9.4.15 |  | P-962 | 18.5/2920 | 6309ZZC3/6309ZZC3 | gtc | tom | Pastillator ground floor
2 | 11.4.15 |  | 07U2G1A | 110/1485 | 6319C3/6316C3 | rnp |  | TP-45 section
3 | 13.4.15 |  | 02G1 | 435/12pole | 6326MC3/6326MC3 | rnp/cpp | Om Sai | H2 compressor house
4 | 25.4.15 |  | P-307B | 15/1450 | 6309C3/6309C3 | gtc |  | DFA Gnd Floor
2015-05-14
1 | 4.5.15 |  | P-36A | 22/2930 | 6310ZZC3/6310ZZC3 |  | rnp | DFA
2 | 7.5.15 |  | P-7122 | 7.5/1440 | 63085ZZC3/6307ZZC3 | rsm/rnp |  | GDP
3 | 9.5.15 |  | 08N14A | 4/1440 | 6206ZZC3/6205ZZC3 | avv/skp | sal | Old Tankfarm
4 | 9.5.15 |  | P-456B | 30/2955 | 6312C3/6212C3 |  |  | Jutasama 3rd floor
5 | 11.5.15 |  | 08N16A | 1.5/1420 |  |  | Sanjayraj | Old Tankfarm
6 | 19.5.15 |  | MCT Bleacher | 4/1440 | 6208ZZC3/6207ZZC3
7 | 21.5.15 |  | Canteen Grinder Mixer | 0.75/90 |  |  | rnp | Canteen A
8 | 26.5.15 |  | P-1012C | 30/2940 | 6311ZZC3/6312ZZC3 | sal | rsm/sal | CPP Terrace
9 | 27.5.15 |  | P-1012A | 30/2940 | 6311ZZC3/6312ZZC3 | sal | rsm | CPP Terrace
10 | 27.5.15 |  | Garden Grass Cutter |  | 6204ZZC3
11 | 30.5.15 |  | P-306B | 11/2840 | 6309ZZC3/6309ZZC3 | skp | sanjayraj | DFA 1st floor
12 | 30.5.15 |  | 23P2 | 15/2940 | 6309C3/6309C3 | sal | sanjayraj | CGS Ground floor
2015-06-14
| 1.06.15 |  | P-30B | 7.5/2900 | 6208ZZC3/6305ZZC3 |  |  | DFA Gnd Floor
| 3.6.15 |  | VP-601A | 11/1400 | 6309ZZC3/6309ZZC3 | avv | rsm/sal
| 5.6.15 |  | P-306B | 11/2940 | 6309ZZC3/6309ZZC3 |  | sal
| 24.6.15 |  | Sm-50 blower | 18.5/2900 | 6309ZZC3/6308ZZC3 |  |  | Old boiler
|  |  | 02G3 | 330kw
| 29.6.15 |  | 05G11B | 11/2pole | 6309ZZC3/6209ZZC3
| 29.6.15 |  | 09U1G15B
2015-07-14
| 6.7.15 |  | P-322A | 18.5/1475 | 6310ZZC3/6310ZZC3 |  | rsg | DFA 2nd Floor
| 7.7.15 |  | P-412B | 11/2930 | 6309ZZC3/6209ZZC3 | gtc |  | DFA gnd floor
| 7.7.15 |  | C-303 | 11/2935 | 6309/6309 | sal |  | FALKER gnd floor
| 8.7.15 |  | 09U1G20 | 11/2920 | 6309ZZC3/6209ZZC3 | avv |  | ETP gnd floor
| 10.7.15 |  | TF-4-32C | 5.5/2980 |  |  |  | Flaker gnd floor
| 11.7.15 |  | P-1012A | 30/2940 | 6311ZZC3/6312ZZC3 | avv |  | CPP 3rd floor
| 14.7.15 |  | P-819B | 5.5/2870 |  |  |  | New TF
| 15.7.15 |  | 03G18A | 15/2920 |  |  |  | FAP 2nd floor
| 17.7.15 |  | 01G11A |  |  |  |  | Stripper gnd floor
| 23.7.15 |  | P-819A | 5.5/2870 |  | CM |  | New TF
| 22.7.15 |  | 01G6A | 7.5/1455 | 639ZZ/6308ZZ |  |  | FAP gnd floor
2015-08-14
| 6.8.15 |  | P-8001A | 5.5/2920 |  | GTC |  | DFA
| 26.8.15 |  | 02G3 | 330/16pole | 6326MC3 | CM | Farhan Electrical | H2 compressor house
| 26.8.15 |  | P-1016A | 15/1450 | 6309ZZC3 | CM | Sanjayraj | CPP Cooling tower CT Fan
| 27.8.15 |  | P-1016B | 15/1450 | 6309ZZC3 | CM | Sanjayraj | CPP Cooling tower CT Fan
| 31.8.15 |  | 02G3G1 | 1.1/1425 | 6206ZZC3 | CM | Ramesh | 02G3 Lub oil pump
2015-09-14
| 3.9.15 |  | 01G12B | 11/1450 | 6308ZZC3/6309ZZC3 | CM | Sal | FAP
| 5.9.15 |  | P-34A | 7.5/2850 | 6308ZZC3/6307ZZC3 |  |  | DFA
| 5.9.15 |  | 01G5B | 30/2955 | 6312C3/6212C3 | Cm | gtc/rnp | FAP
| 12.9.15 |  | P-710B | 5.5/1450 | 6308ZZC3/6208ZZC3 |  | rsg | Loop Reactor
| 16.9.15 |  | CGS -Agitator motor | 0.75/315 |  |  | rsg/cpp | CGS
2015-10-14
| 1.10.15 |  | 01G1A | 55/2950 | 6315C3/6215C3 | CM | rnp | FAP ground floor
| 2.10.15 |  | 03G17B |  | 6311ZZC3/6312ZZC3 |  | cpp/skp
| 10.10.15 |  | 06G1A | 90/4pole |  | CM
| 10.10.15 | Dozing pump | 10U2G1 |  | 6202ZZ/6202ZZ |  | rnp
| 14.10.15 |  | P-422B | 22/2940 |  |  |  | DFA 2nd floor
| 15.10.15 |  | P-7117 | 5.5/2905 | 6206ZZC3/6206ZZC3 | gtc | sal | GDP Ground Floor
| 24.10.15 |  | BFW-1 IAEC Boiler | 18.5/2920 | 6309C3/6309C3 | rsg | GTC | New boiler
| 25.10.15 |  | P-366 |  | 6205ZZC3/6205ZZC3 |  |  | DFA 7th floor
2015-11-14
| 4.11.15 |  | P-150.3 | 3.7/2900 | 6306ZZC3/6306ZZC3 | rnp |  | CGS Ground floor
|  |  | P-515B | 18.5/2920 | 6309ZZC3/6209ZZC3 |  |  | DFA
| 16.11.15 |  | 03G18B |  | 6309ZZC3 |  | sal
| 19.11.15 |  | P-431B | 18.5/2910 | 6209ZZC3 | rnp | rnp | DFA 2nd Floor
| 20.11.15 |  | Single phase motor dosa mixer |  |  |  |  | Canteen A
| 20.11.15 |  | CGS filter press hydraulic motor | 2.2/1415 | 6205ZZC3/6206ZZC3 | rsm | rsm | CGS Ground floor
| 20.11.15 |  | TF-4/32C | 5.5/2880 | 6306ZZC3/6205ZZC3 | gtc |  | TF-4
| 25.11.15 |  | New boiler pit pump | 2.2/2880 | 6205ZZC3 |  |  | New boiler
2015-12-14
| 1.12.15 |  | Vibro Feeder | 0.37 | Roller Bearing | CHP operator | Sanjay Raj | CHP plant
| 2.12.15 |  | 01G17A | 1.5/2825 | 6205ZZC3 | RSG | SAL | Alcohol 3rd floor
| 4.12.15 |  | C-403 | 1.5/2826 | 6309ZZC3/6309ZZC3 | CPP | CPP | Flaker
| 19.11.15 |  | P-655 | 22/2910 | 6310ZZC3 | CM | SAL | Alfa Postcon
| 20.11.15 |  | 01G19B | 15/2920 | 6309ZZC3/6209ZZC3 | CM | SAL | Stipper ground floor
| 20.11.15 |  | P-3A | 3.7/2930 | 6206ZZC3/6306ZZC3 | CM | SAL | K-3 2nd floor
| 20.11.15 |  | Spare | 30 | 6313ZZC3 |  | DLK | Spare
| 25.11.15 |  | Spare | 5.5/2835 | 6306ZZC3 |  | RSG
2016-01-01
| 9.1.16 |  | BDG-1 | 0.37 |  |  | RSM | old Boiler
| 15.1.16 |  | P-420 | 1.5 |  | CM | RSM | MCC 103
| 16.1.16 |  | 05G9G | 30 | 6312ZZC3/6312ZZC3 | CM | RSM | old Boiler
| 12.1.16 |  | C-402 | 11 | Planned for next month
| 20.1.16 |  | VP-651B | 15 | 6309ZZC3/6209ZZC3 | SAL | SAL | Postcon
| 27.1.16 |  | Spare motor | 15 | 6309ZZC3/6209ZZC3 |  | SAL
2016-02-02
| 2.2.16 |  | P-309B | 2.2 | 6205ZZC3/6205ZZC3 | RSG | RSG | DFA Ground Floor
| 2.2.16 |  | Spare Motor | 2.2 | 6205ZZC3/6205ZZC4 | RSG | RSG | DFA Ground Floor
| 7.2.16 |  | P-307A | 15 | 6309C3/6309C3 | GTC | SAL | DFA Ground Floor
| 22.2.16 |  | P-802A | 15 | 6209ZZC3/6209ZZC3 | RSG | RSM/GTC | Loop Reactor Ground
| 25.2.16 |  | 03G3A | 11 | 6308ZZC3/6309ZZC3 | CM | SAL
| 25.2.16 |  | 05G13 | 30 | 6312ZZC3/6212ZZC3 | RSM | RSM | Water Tank Area Boiler
| 29.2.16 |  | 03G1B | 55 | 6315C3/ 6215C3 | CPP | CPP
2016-03-02
| 12.03.16 |  | P-320B | 22 | 6210C3/6210C3 | CM | SAL | DFA Ground Floor
| 15.3.16 |  | P-651A | 15 | 63090C3/6309C3 | GTC | SAL | DFA Ground Floor
| 16.3.16 |  | DAA | 7.5 | 6208ZZC3/6208ZZC3 | CM | SAL | ETP
| 16.3.16 |  | DAF | 7.5 | 6208ZZC3/6208ZZC3 | CM | SAL | ETP
| 17.3.16 |  | P-802B | 15 | 6209ZZC3/6309ZZC3 | CM | RNP | Loop Reactor Ground
| 25.3.16 |  | 05G9F | 30 | 6312ZZC3/6212ZZC3 | CM | SAL | Old Boiler Utility ground floor
| 31.3.16 |  | P-1050A2 | 150 | 6319C3 ( DE Side) only | CM | SAL/RANA | Coal heater ground floor
2016-04-02
| 2.4.16 |  | 06G1G Dryer Motor | 0.55 | 6002ZZ/6002ZZ | Vendor | SAL | DFA Air Compressor
| 22.4.16 |  | 06G1D | 75 | NU215ECP/ 6215 /C4VT269 | CM | Sanjay Raj | Air Compressor
| 16.3.16 |  | 20P07B | 15 | 6309ZZC3 / 6209ZZC3 | CM | SAL | ETP
2016-05-02
| 1.5.16 |  | 03G17A | 22 | 6312ZZC3/6211ZZC3 | CM | RNP | alochol
| 20.5.16 |  | 20P03A | 110 | 6316C3/6319C3 | Varun | SAL/RNP | Fatty Acid
| 22.5.16 |  | 05G3C | 3.7/2900 | 6205ZZC3/6206ZZC3 | CPP | SAL/RNP | Utility
| 22.5.16 |  | 910B | 7.5/2850 | 6308ZZC3/6307ZZC3 | CM | AVV/RSG | Fatty Acid
| 13.5.16 |  | P - 1012A | 30/2900 | 6311ZZC3/6312ZZC3 | CM | RNP | CPP
2016-06-16
| 20.6.16 |  | P-1050B1 |  | BEARING CLEANED | CM | RSM/AVV
| 22.6.16 |  | P-513B |  | 6312ZZ,6212ZZC3 | CM | RNP/GTC | K4
| 25.6.16 |  | P-802C | 18.5/2930 | 6312ZZ,6212ZZC3 | CM | SAL/BHP | TF
| 25.6.16 |  | P-705B | 55/989 | 6318C3 | SPARE | SAL | Loop Reactor Ground
2016-07-01
2016-08-01
1 | 01.08.16 |  | P-516A | 2.2/2900 | 6205ZZ/ 6205ZZ | CM | RSG/SAL | K4
2 | 11.08.16 |  | 09U1G21 | 5.5/2900 | 6208ZZ/6208ZZ | CM | RSM/DLK | ETP
3 | 13.08.16 |  | 10G02 | 9.3/1400 | 6309ZZ/6209ZZ | CM | CPP/DLK | CALORIC
4 | 13.08.16 |  | BL-1301 | 3.7/1400 | - | CM | CPP/DLK | SYNDENT
5 | 17.08.16 |  | 01G5B | 30/2900 | 6312ZZ/ 6212ZZ | CM | SAL/BHP | FAP GF
6 | 24.08.16 |  | FLACKER MOTOR-SION | 22/2900 | 6210ZZ/ 6210ZZ | SION | BHIM | SION
7 | 24.08.16 |  | GDP MOTOR-SION | 11./2900 | 6309ZZ/6209ZZ | SION | RNP/CPP | SION
8 | 28.08.16 |  | DEGASER BLOWER | 0.37/2900 | 6203ZZ/ 6203ZZ | UTILITY | - | UTILITY
2016-09-01
1 | 11.09.16 |  | Utility Blower | 0.75/1440 | 6204 C3/ 6204 C3 | UTILITY | BHIM | UTILITY
2 | 13.09.16 | High Pressure Fat / Water Feed Pump | P-602B | 2.2/ 2900 | 6205ZZ/ 6205ZZ | RSM | SAL/AVV | Precon
3 | 15.09.16 | Raw water pump-2 | 20P07B | 15/2900 | 6309 ZZ C3/ 6309 ZZ C3 | CM | RSM | RAW WATER
4 | 19.09.16 | Linde ID fan | F-101 | 30/2900 | 6312 ZZ C3/ 6212 ZZ C3 | CM | SAL/RNP | LINDE
5 | 17.09.16 | K-3 bottom product transferring pump | P-30A | 15/2900 | 6309 ZZ C3/ 6309 ZZ C3 | CM | BHIM | K3
6 | 22.09.16 | D-10 to K-3 | P-4A | 22/2900 | 6310 ZZ C3/6310 ZZ C3 | CM | RSG/DLK | DFA
7 | 21.09.16 | Linde FD fan | F-102 | 7.5/2900 | 6307 ZZ C3/ 6308 ZZ C3 | CM | SAL/ RSG | LINDE
8 | 29.09.16 | Condensate transfer pump-1 | P-816A | 1.1/2900 | 6204 ZZ/ 6204 ZZ | CPP | RNP/AVV | TANKFARM
2016-10-01
1 | 03.10.16 | Water Charge Pump. | P-203 | 22/1440 | 6311 ZZ C3/ 6312 ZZC3 | CM | SAL | DFA
2 | 25.10.16 | Hotwell Pump | P-360B | 37/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | AVV/ SAL | JUTASAMA
3 | 08.10.16 | CHILLED WATER PUMP | P-304 | 11./2900 | 6309ZZ/6209ZZ | CM | RSG/GTC | FLACKER
4 | 27.10.16 | AUX.AIR FAN B | P-1001B | 2.2/2900 | 6205 ZZ/ 6205 ZZ | CPP | SAL | CPP
5 | 27.10.16 | AUX.AIR FAN A | P-1001A | 2.2/2900 | 6205 ZZ/ 6205 ZZ | CPP | AVV/GTC | CPP
6 | 27.10.16 | HOT WATER PUMP-2 | P-1015B | 11./2900 | 6309ZZ/6209ZZ | CPP | SAL/RANA | CPP
6 | 29.10.16 | CW supply Pump for Splitting & SW | P-9002B | 80/1440 | 6316 C3/ 6316 C3 | AVV | SAL/RANA | SPLITTING
2016-11-01
1 | 05.11.16 | K-3 Reboiler thermic fluid circulation pump | P-36A | 22/2900 | 6310ZZ C3/ 6310 ZZ C3 | SAL | SAL | DFA
2 | 12.11.16 | Clean CW Pump -Precon & Postcon | P-364A | 75/1450 | 6317 C3/ 6317 C3 | CM | CPP/RANA | JUTASAMA
3 | 14.11.16 | PESTILLATOR AHU | AHU Motor | 5.5/2900 | 6308 ZZ C3/ 6308 ZZ C3 | TOM | Sanjayraj | Pestillator
4 | 19.11.16 | Forklift-2 | Stering Motor | 0.65/2100 | 6006 ZZ/ 6202 ZZ | RSM | Sanjayraj | Pestillator
5 | 16.11.16 | Terpered cooling water I pump | 05G10B | 90/2900 | 6316 C3/ 6319C3 | CM | CPP/ RSG | Acid Stripper
6 | 23.11.16 | DM water pump | P-363A | 11/2900. | 6209 ZZ C3/ 6309 ZZ C3 | CM | CPP | JUTASAMA
7 | 25.11.16 | Circulation pump | 03G15B | 18.5/2900 | 6309 ZZ C3/ 6310 ZZ C3 | BHP | RNP | FAP GF
8 | 28.11.16 | COOLING TOWER PUMP-A | P-1012A | 30/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | RSM | CPP
9 | 28.11.16 | COOLING TOWER PUMP-B | P-1012B | 30/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | RSM | CPP
10 | 29.11.16 | COOLING TOWER PUMP-C | P-1012C | 30/2900 | 6311 ZZ C3/ 6312 ZZC3 | CM | RSM | CPP
11 | 29.11.16 | COOLING WATER GT PUMP-B | P-1017B | 7.5/2900 | 6307 ZZ C3/ 6308 ZZ C3 | CM | RSG | CPP
12 | 29.11.16 | SAF GD-03 | P-1008 | 1.5/2900 | 6205 ZZ/ 6205 ZZ | CM | RSM | CPP
2016-12-01
1 | 01.12.16 | L.P.condensate pump | 07G1B | 1.5/ 2900 | 6203 ZZ C3/ 6203 ZZ C3 | AVV | RSG/CPP | Alcohol
2 | 08.12.16 | Dryer Circulation Pump | P-431A | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | RANA | DFA
3 | 11.12.16 | Crude oil transfer pump-1 | P-802A | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | T/F | CPP | TANKFARM
4 | 12.12.16 | Crude oil transfer pump-3 | P-802C | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | CPP | TANKFARM
5 | 17.12.16 | Circulation pump for 01D1 | 01G1A | 55/2900 | 6315 C3/ 6215 C3 | CM | CPP/BHP | Alcohol
6 | 25.12.16 | Boiler feed water pump 3TPH | 07U1G2B | 7.5/ 2900 | 6206 ZZ C3/ 6308 ZZ C3 | Old Boiler | RSG | Old Boiler
2017-01-01
1 | 10.01.17 | Hotwell pump | D-1-1 | 30/2900 | 6311 ZZ C3/ 6311 ZZ C3 | CM | SAL | DFA
2 | 10.01.17 | Air Blower 16-A | 09U1G16A | 55/ 1440 | 6215 C3/ 6215 C3 | ETP | SAL | ETP
3 | 10.01.17 | Intermediate Transfer Pump | 08G20 | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | CM | SAL | T/F GR. FLOOR
4 | 12.01.17 | Trolly Unloading Pump-1 | P-801A | 5.5/ 2900 | 6208 ZZ C3/ 6208 ZZ C3 | CM | SAL | LOOP REACTOR
5 | 16.01.17 | Pestillator Forklift Stering Motor | Stering Motor | 0.65/ 2100 | 6303 ZZ C3/ 6006 2RS | Pestillator | SAL | Pestillator
6 | 14.01.17 | High Pressure Fat Feed Pump | P-201 | 30/1440 | 6213 ZZ C3/ 6212 ZZ C3 | CM | SAL | Splitting
7 | 16.01.17 | HOT WATER PUMP-1 | P-1015A | 18.5/2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | SAL | CPP
8 | 31.01.17 | Collective Water Pump (T/F) | P-832 | 7.5/ 2900 | 6307 ZZ C3/ 6308 ZZ C3 | New T/F | SAL | New T/F
2017-02-01
1 | 02.02.17 | Water ring vacuum pump | VP-27A | 15/2900 | 6309 ZZ C3/ 6309 ZZ C3 | CM | SAL | DFA
2 | 04.02.17 | HOT WATER PUMP-1 | P-1015A | 18.5/2900 | 6209 ZZ C3/ 6309 ZZ C3 | CM | SAL | CPP
3 | 04.02.17 | H2 Compressor | 02G1A | 470/495 | 6326 M C3/ 6326 M C3 INSULATED | - | DOL ELECT. | H2 COMP.
4 | 05.02.17 | RO Cartridge feed Pump | 09U1G25 | 5.5/2900 | 6208 ZZ C3/ 6208 ZZ C3 | ETP | SAL | ETP
5 | 05.02.17 | Crude oil transfer pump-3 | P-802C | 18.5/ 2900 | 6209 ZZ C3/ 6309 ZZ C3 | T/F | BHP | TANKFARM
6 | 06.02.17 | F.D.Fan | 10G01C | 160/2900 | 6316 C4/ 6316 C4 | CM | SAL | ALCOHOL
7 | 07.02.17 | BWF pumps | 10G04A | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | SAL | ALCOHOL
8 | 09.02.17 | BWF pumps | 10G04B | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | SAL | ALCOHOL
9 | 16.02.17 | Air Blower | 09U1G17 | 18.5/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | SAL | ETP
10 | 28.02.17 | D-20 DM water V-303 | P-34A | 7.5/2900 | 6207 ZZ C3/ 6208 ZZ C3 | DFA | SAL | DFA
2017-03-01
1 | 05.03.17 | FORCED DRAFT FAN - 1 | P-1052A | 125/1440 | 6319 C3/ 6319 C3 | CHP | SAL | CHP
2 | 06.03.17 | Condensate Transfer Pump | P-8001B | 5.5/2900 | 6208 ZZ C3/ 6208 ZZ C3 | CM | RSM | PRECON
3 | 09.03.17 | ETP Pit Pump | P-913B | 2.2/2900 | 6205 ZZ C3/ 6205 ZZ C3 | - | CPP | OLD BOILER
4 | 12.03.17 | Intermediate FA transfer pump | 08G5B | 30/2900 | 6212 ZZ C2/ 6313 ZZ C3 | - | RSM | TANKFARM
5 | 16.03.17 | CT FAN-1 | P-1016A | 15/1440 | 6309 ZZ C3/ 6309 ZZ C3 | - | RNP | CPP
6 | 22.03.17 | Reboiler circulation pump-1 | P-307A | 15/1440 | 6309 ZZ C3/ 6309 ZZ C3 | - | RNP | DFA
7 | 22.03.17 | Hot oil circulation pump-2 | P-312B | 18.5/1440 | 6310 ZZ C3/ 6310 ZZ C3 | - | SAL | DFA
8 | 23.03.17 | H2 Compressor lubricator | 02G1G3 | 0.25/1400 | 6202 ZZC3/ 6004 ZZ C3 | - | CPP | H2 COMP.
9 | 27.03.17 | BWF pumps | 10G04B | 22/2900 | 6210 ZZ C3/ 6210 ZZ C3 | - | CPP/ SAL | ALCOHOL
10 | 29.03.17 | Hot oil dooster pump-2 | P-318B | 5.5/2900 | 6206 ZZ C3/ 6206 ZZ C3 | - | RNP | DFA

## Burnt motor (hidden)
Sr.No. | DATE | Equipment Name | MOTOR TAG | M/C NO. | KW | RPM | Bearing No. | Reported By | SENT TO | Location | Reason
1 | 12.05.14 | DEODERIZER DRYER RECIRCULATION PUMP | P-7102 |  | 2.2 | 2900 |  |  | SANJAY RAJ ELECTRICAL | GDP
2 | 29.05.14 | SAF GD-03 | P-1008 |  | 4 | 2950 | 6306/ZZC3 | SAL | SANJAY RAJ ELECTRICAL | CPP
3 | 16.06.14 | ETP Three Phase submersible pump | [6 empty] | SANJAY RAJ ELECTRICAL | ETP
4 | 10.07.2014 | Utility DM Agitator |  |  | 0.55 | 910 |  | SAL/CPP | SANJAY RAJ ELECTRICAL | Old Boiler
5 | 19.7.2014 |  | P-655 |  | 22 | 1475 | 6310ZZC3 | CPP | SANJAY RAJ ELECTRICAL | CGS
6 | 3.08.2014 | X-FER PUMP FROM HOT WELL TO COOLING WATER | P-7114B |  | 18.5 | 2910 | 6309ZZC3/6308ZZC3 | CPP/SKP | SANJAY RAJ ELECTRICAL | GDP gnd floor
7 | 13.10.14 | Froced draft fan bioler 3TPH | 07U1G1B |  | 11 | 2910 | 6209ZZC3 | CPP/SKP | SANJAY RAJ ELECTRICAL | Utility
8 | 3.11.2014 | CPP CT fan-2 | P-1016B |  | 15 | 1450 | 6309ZZC3 | RSM | SANJAY RAJ ELECTRICAL | CPP
9 | 9.11.2014 | DEODERIZER DRYER RECIRCULATION PUMP | P-7102 | Sr no-72525 | 2.2 | 2840 |  | cpp/skp | SANJAY RAJ ELECTRICAL | GDP
10 | 9.11.2014 | DC hydraulic motor of forklift |  |  | 7.5kw |  |  | cpp | SANJAY RAJ ELECTRICAL | Flaker
11 | 06.12.14 | Agitator for 08T9C | 08N14C |  | 4 | 1440 |  | CPP/SKP | SANJAY RAJ ELECTRICAL | Old tankfarm
12 | 16.12.14 | CPP Seal Air Fan | P-1008 |  | 4 | 2950 | 6306ZZC3 | RSG/DLK | SANJAY RAJ ELECTRICAL | CPP gnd floor
13 | 25.12.14 | Vaccum pump | VP-451B |  | 11 | 1450 | 6309ZZ/6209ZZ | BBL | SANJAY RAJ ELECTRICAL | Jutasama 6th floor
14 | 21.3.15 |  | P-802B |  | 15 | 2930 | 6309ZZC3/6209ZZC3 | BBL | SANJAY RAJ ELECTRICAL | LOOP ground floor
15 | 24.3.15 |  | X-201 |  | 7.5 | 1440 | 6308ZZC3/6208ZZC3 | kirloskar | SANJAY RAJ ELECTRICAL | DFA 5th floor
16 | 26.4.15 |  | P-309B | N2409591 | 9.3 | 2930 | 6208ZZC3 | BBL | SANJAY RAJ ELECTRICAL | DFA gnd floor
17 | 30.5.15 | Agitator for Tank-828 | Tank-828 Agitator | 32391 | 3.7 | 960 | 6308ZZC3/6307ZZC3 | ABB | SANJAY RAJ ELECTRICAL | New TF
18 | 6.5.15 |  | 08N18A |  | 2.2 | 1420 |  |  | SANJAY RAJ ELECTRICAL | Old TF
19 | 26.6.15 |  | P-515B | [5 empty] | SANJAY RAJ ELECTRICAL
20 | 8.7.15 | Mix bed blower motor |  |  | 2.2 | 1425 |  | SAL | SANJAY RAJ ELECTRICAL | Old boiler
21 | 6.9.15 |  | P-168.5 |  | 0.75 | 935 | 6205ZZC3 |  | SANJAY RAJ ELECTRICAL | CGS gnd floor
22 | 23.8.15 |  | P-515B |  | 18.5 | 2920 | 6309ZZC3/6209ZZC3 | cpp
23 | 11.10.15 | Recycle Compressor | 02G3 |  | 330 | 16pole | 6326MC3 | avv | DOL Electric | H2 compressor house
24 | 12.3.16 | Vaccum pump Alfa level Postcon | P-651A |  | 15KW | 4 | 63092RS/6209-2RS | RSG/DLK | SANJAY RAJ ELECTRICAL | Alfa Level Postcon
25 | 11.3.16 | Septic Pump | Septic |  | 1.5KW | NA | NA | RNP/GTC | SANJAY RAJ ELECTRICAL | ETP
26 | 9.3.16 | Pit pump |  |  | 0.55 | 2 | NA | AVV | SANJAY RAJ ELECTRICAL | Pit pump Alcohol
27 | 10.3.16 | E-Wax Agitator | E-Wax |  | NA | NA | NA | RNP/GTC | SANJAY RAJ ELECTRICAL | Patillator
28 | 3.3.16 | Agitator Motor 09U1G21A | 09U1G21A |  | 5.5 | 2 | 6208ZZC3 | RSM/CPP | SANJAY RAJ ELECTRICAL | ETP
29 | 2.4.16 | 06G1G Dryer motor | Dryer Motor |  | 0.55 |  | 6002ZZ | SAL | SANJAY RAJ ELECTRICAL | DFA Air Compressor
30 | 22.4.16 | Safex Motor Hoist | Hoisting motor |  | 1.1 | 1400 | NA | Subhash | SANJAY RAJ ELECTRICAL | Coal Heater
31 | 12.5.16 | Cooling water motor | 20P03B |  | 110 | 1485 | 6319C/6316C3 | RSM | PO work in progress | GDP
32 | 20.5.16 | Hydrogen Compressor Motor | 02G1 |  | 435 | 480 | 6326MC3/6326MC3 | RSM/RSG | DOL Electric | H2 compressor house
33 | 2016-06-16 | NO ANY MOTOR BURNT
34 | 05.07.16 | Cold well pump to steel belt | P-961 |  | 18.5 | 2900 | 6309ZZ/6209ZZ | RNP | SANJAY RAJ ELECTRICAL | Pestillator
35 | 20.08.16 | Decoderizer dryer pump | P-7102 |  | 2.2 | 2900 | - | BHIM | SANJAY RAJ ELECTRICAL | -
36 | 08.09.16 | TANKFARM FEED PUMP | P-7100A |  | 9.3 | 2900 | 6308ZZ/ 6308ZZ | BHIM | SANJAY RAJ ELECTRICAL | GLYCERIEN
37 | 22.10.16 | E-13 Condensate transferring pump | P-31B |  | 7.5 | 2900 | - | CPP | SANJAY RAJ ELECTRICAL | DFA 3RD FLOOR
38 | 27.10.16 | AUX.AIR FAN B | P-1001B |  | 2.2 | 2900 | 6205 ZZ/ 6205 ZZ | CPP/ RSM | SANJAY RAJ ELECTRICAL | CPP
39 | 10.11.16 | TANK FORM FEED PUMP | P-7100A |  | 9.3 | 2900 | 6308ZZ/ 6308ZZ | BHIM | SANJAY RAJ ELECTRICAL | GLYCERIEN | Motor Bearing was jam
40 | 15.11.16 | Air compressor | 06G1A |  | 90 | 1440 | 6317 C3/ 6317 C3 | CPP | DOL Electric | Utility | Winding insulation fail.
41 | 15.11.16 | Spare 110 KW motor |  |  | 110 | 2900 | 6316 C3/ 6319 C3 |  | DOL Electric | Utility | Winding insulation fail.
42 | 24.11.16 | Vaccum Pump | VP-7103B |  | 5.5 | 1440 | - | RSM | SANJAY RAJ ELECTRICAL | GLYCERIEN | Winding resistance unbalance
43 | 19.12.16 | ATFD FEED PUMP | P-7120 |  | 3.7 | 2900 | 6206 ZZ C3/ 6206 ZZ C3 | DLK | SANJAY RAJ ELECTRICAL | GDP | Winding insulation fail.
44 | 16.01.17 | Pestillator Forklift Stering Motor | Stering Motor |  | 0.65 | 2100 | 6303 ZZ C3/ 6006 2RS | AVV | SANJAY RAJ ELECTRICAL | Pestillator | Winding insulation fail.
45 | 03.02.17 | Hot well to Cooling tower pump | 01G19B |  | 18.5 | 2900 | 6209 ZZ C3/6309 ZZ C3 | RSM | SANJAY RAJ ELECTRICAL | ALCOHOL | Motor Bearing was jam
46 | 15.02.17 | CT FAN-2 | P-1016B |  | 15 | 1400 | 6209 ZZ C3/6309 ZZ C3 | RNP/CPP | SANJAY RAJ ELECTRICAL | CPP | Motor bearing housing fully rubbed & rotor touched to stator
47 | 19.02.17 | Degasser Blower | Degasser Blower |  | 0.37 | 2900 | - | CPP | SANJAY RAJ ELECTRICAL | Old Boiler | Winding insulation fail.
48 | 20.02.17 | ETP Three Phase submersible pump | ETP Submerge Pump |  | 2.2 | 2900 | - | DLK | SANJAY RAJ ELECTRICAL | ETP | Winding resistance unbalance
49 | 23.02.17 | Condensate Pump | 07G7B |  | 0.55 | 2900 | - | CPP | SANJAY RAJ ELECTRICAL | ALCOHOL | Moisture inside Motor
50 | 01.03.17 | Feed pump to D-10 | P-3B |  | 3.7 | 2900 | 6206 ZZ C3/ 6206 ZZ C3 | CPP | SANJAY RAJ ELECTRICAL | DFA | Winding insulation fail.
51 | 01.03.17 | RESIDUE TRANSFER PUMP | P-7104A |  | 3.7 | 2900 | 6206 ZZ C3/ 6206 ZZ C3 | DLK | SANJAY RAJ ELECTRICAL | GDP | Winding insulation fail.
52

## Mechanical
PM(FY 16-17)
|  | DFA |  | FAP
Sr. NO. | Months | Planned | Actual | Planned | Actual
1 | April'16 | 52 | 52 | 52 | 52
2 | May'16 | 52 | 52 | 45 | 45
3 | June'16 | 52 | 52 | 52 | 52
4 | July'16 | 52 | 52 | 52 | 52
5 | Aug'16 | 51 | 51 | 52 | 52
6 | Sept'16 | 51 | 51 | 52 | 52
7 | Oct'16 | 51 | 51 | 52 | 52
8 | Nov'16 | 51 | 51 | 52 | 52
9 | Dec'16 | 51 | 51 | 52 | 52
10 | Jan'17 | 60 | 55 | 76 | 63
11 | Feb'17 | 60 | 35 | 65 | 31
12 | Mar'17 | 60 | 23 | 74 | 15
Total |  | 643 | 576 | 676 | 570
|  |  | 89.5801 |  | 84.3195

## Sheet2 (hidden)
TAG NO. | DESCRIPTION
125.8 | Talc system Dosing pump
128.17 | Spent lye feed pump
128.4 | Water feed pump
201.2 | Soap transfer pump
Old Flakar Drum Motor
01G10A | wax ester pump
01G10B | wax ester pump
01G11A | 01D11 Transfer Pump
01G11B | 01D11 Transfer Pump
01G12A | LIQUID RING VACCCUM PUMP
01G12B | LIQUID RING VACCCUM PUMP
01G13 | Reactor Drain out pump
01G13A | Thermic fluid pump for stripper
01G13B | Thermic fluid pump for stripper
01G14A | Tempered water pump-III
01G14B | Tempered water pump-III
01G15A | 01D10 Circulation Pump
01G15B | 01D10 Circulation Pump
01G16A | Tempered cooling water III pump
01G16B | Tempered cooling water III pump
01G17A | Scrubber Pump( FAP 3rd Floor)
01G17B | Scrubber Pump( FAP 3rd Floor)
01G18A
01G19A | Hot well to Cooling tower pump
01G19B | Hot well to Cooling tower pump
01G1A | Circulation pump for 01D1
01G1B | Circulation pump for 01D1
01G20
01G2A | Circulation pump for 01D2
01G2B | Circulation pump for 01D2
01G3A | Circulation pump for 01D3
01G3B | Circulation pump for 01D3
01G4A | Circulation pump for 01D4
01G4B | Circulation pump for 01D4
01G5A | Inline pump for 01E1
01G5B | Inline pump for 01E1
01G6A | Inline pump for 01E2
01G6B | Inline pump for 01E2
01G7A | Inline pump for 01E3
01G7B | Inline pump for 01E3
01G8A | Inline pump for 01E4
01G8B | Inline pump for 01E4
01G9A | 01E8 Thermic fluid circulation pump-1
01G9A | Inline pump for 01E8
01G9B | Inline pump for 01E8
01G9B | 01E8 Thermic fluid circulation pump-1
02G1 | H2 Compressor
02G1A | H2 Compressor
02G1AG1 | H2 Compressor main lub oil pump
02G1AG2 | H2 Compressor Aux.lub oil pump
02G1AG3 | H2 Compressor lubricator
02G1G1 | H2 Compressor main lub oil pump
02G1G2 | H2 Compressor Aux.lub oil pump
02G1G3 | H2 Compressor lubricator
02G3 | Recycle Compressor
02G3G1 | Recycle Comp. main lub oil pump
02G3G2 | Recycle Comp. Aux. lub oil pump
02G3G3 | Recycle Compressor lubricator
02G5A | HP wax ester feed pump
02G5AG1 | HP wax sealing pump motor
02G5B | HP wax ester feed pump
02G5BG1 | HP wax sealing pump motor
02G5C | HP wax ester feed pump
02G5CG1 | HP wax sealing pump motor
02G7A | Crude alcohol pump
02G7B | Crude alcohol pump
02G7C | Booster Pump
02G8A | Section-3 feed pump-1
02G8B | Section-3 feed pump-1
03G11A
03G14A | Residue recycle pump
03G14B | Residue recycle pump
03G15A | Circulation pump
03G15B | Circulation pump
03G16G3 | WR Vaccum pump
03G17A | Hot Well Pump
03G17A | Main distillated pump-1
03G17B | Hot Well Pump
03G17B | Main distillated pump-2
03G17C | Main distillated pump-3
03G1A | Circulation pump drive cycle
03G1B | Circulation pump drive cycle
03G2A | Pump for Distillate
03G2B | Pump for Distillate
03G3A | Pump for column 03D2
03G3B | Pump for column 03D2
03G4A | Inline pump for thermal oil
03G4B | Inline pump for thermal oil
03G5A | Pump for fraction from 03D2
03G5B | Pump for fraction from 03D2
03G5C | Pump for fraction from 03D2
03G6A | Inline pump for thermal oil
03G6B | Inline pump for thermal oil
03G7A | Pump for final Residue
03G7B | Pump for final Residue
03G8A | Inline pump for thermal oil
03G8B | Inline pump for thermal oil
03G9A | Inline pump for thermal oil
03G9B | Inline pump for thermal oil
04G1B
04G5A | Product pump
04G5B | Product pump
05G10A | Terpered cooling water I pump
05G10B | Terpered cooling water I pump
05G11A | Terpered cooling water II pump
05G11B | Terpered cooling water II pump
05G12A | Hot water pump-1
05G12B | Hot water pump-1
05G18A | New DM water pump-1
05G18B | New DM water pump-1
05G1A | Raw water pump
05G1B | Raw water pump
05G3A | DM water pump
05G3B | DM water pump
05G3C
05G5A | Drinking water pump
05G5B | Drinking water pump
05G7A | Fire water pump
05G8 | Jockey pump
05G9A | Cooling water pump
05G9B | Cooling water pump
05G9C | Cooling water pump
05G9D | Cooling water pump
05G9E | Cooling water pump
05G9F | Cooling water pump
05G9G | Cooling water pump
05U1G1 | Deasser blower
05U1G2 | Mixed bed blower
05U1G3 | Degassor water pump
05U1G7A | Agitator for 05U1T2A
05U1G7B | Agitator for 05U1T2B
05U1G8 | Effluent transfer pump
05U2G1A | C.T.Unit with fans
05U2G1B | C.T.Unit with fans
05U5G1 | Blower for side stream filter
06G1A | Air compressor
06G1B | Air compressor
06G1C | Air compressor
06G1D | Air compressor GA75VSD
06G1E | Air compressor GA55VSD
06G1F | Air compressor GA55
06G1G | Air compressor GA55VSD
06G2 | N2 Booster compressor
07G1A | L.P.condensate pump
07G1B | L.P.condensate pump
07G2A | FO/LSHS Unloading pump
07G3A | LDO transfer pump
07G3B | LDO transfer pump
07G4A | LDO transfer pump
07G5A | FO/LSHS Unloading pump
07G5B | FO/LSHS Unloading pump
07G7A | CONDENSATE PUMP
07G7B | CONDENSATE PUMP
07G8A | CONDENSATE PUMP
07G8B | CONDENSATE PUMP
07U1G1A | Froced draft fan bioler 5TPH
07U1G1B | Froced draft fan bioler 3TPH
07U1G2A | Bioler feed water pump 3TPH
07U1G2B | Bioler feed water pump 3TPH
07U1G3A | Bioler feed water pump 5TPH
07U1G3B | Bioler feed water pump 5TPH
07U1G5A | Fuel oil pump 5TPH
07U1G5A | Fuel oil pump 3TPH
07U1G5B | Fuel oil pump 5TPH
07U1G5B | Fuel oil pump 3TPH
07U1G7A | Ring main pump
07U1G7B | Ring main pump
07U1G8 | Agitator for doasing
07U2G1A | Thermic fluid pump
07U2G1B | Thermic fluid pump
07U2G2A | Forced draft fan
07U2G2B | Forced draft fan
07U2G5 | Sump pump
07U2G6A | Ring main pump
07U2G6B | Ring main pump
07U2G7A | LSHS/FO fuel pump
07U2G7B | LSHS/FO fuel pump
07U2G7C | LSHS/FO fuel pump
07U2G7D | LSHS/FO fuel pump
07U2G8A | LDO fuel pump
07U2G8B | LDO fuel pump
07U3G1C | Circulation pump
07U3G1D | Circulation pump
07U3G2C | FD fan
07U3G3C | Furnace oil pump
07U3G3D | Furnace oil pump
07U3G4C | ring main pump
07U3G4D | ring main pump
07U3G6C | LDO pump
08G10A | Naphtha transfer pump vertical
08G13A | Naphtha unloading pump
08G14D | Agitator for 08T9D
08G14D | Agitator for 08T9D
08G1A | Fatty acid unloading pump
08G1B | Fatty acid unloading pump
08G1C | Fatty acid unloading pump
08G20 | Intermediate Transfer Pump
08G21 | Intermediate Transfer Pump
08G22 | Intermediate Transfer Pump
08G23 | Intermediate Transfer Pump
08G24 | Intermediate Transfer Pump
08G25 | Intermediate Transfer Pump
08G2A | Fatty acid transfer pump
08G2B | Fatty acid transfer pump
08G3A | Fatty Alcohol product filling pump
08G3B | Fatty Alcohol product filling pump
08G3C
08G4A | Wax transfer pump
08G5A | Intermediate FA transfer pump
08G5B | Intermediate FA transfer pump
08G6A | Light end filling pump
08G7A | Residue filling pump
08G8A | Naphtha transfer pump
08G8B | Naphtha transfer pump
08G9A | Naphtha transfer pump Vertical
08N14A | Agitator for 08T9A
08N14B | Agitator for 08T9B
08N14C | Agitator for 08T9C
08N14D
08N15A | Agitator for 08T007
08N16A | Agitator for 08T005
08N17A | Agitator for 08TGA
08N17B | Agitator for 08TGB
08N17C | Agitator for 08TGC
08N17D | Agitator for 08TGD
08N17E | Agitator for 08T4E
08N18A | Agitator for 08T3A
08N18B | Agitator for 08T3B
09G2 | Soap pump for process
09G3 | Soap pump for process
09G4 A | Effluent transfer pump
09G4 B | Effluent transfer pump
09G4 C | Effluent transfer pump
09G5 | Effluent transfer pump
09U1D14 | Centrifuge
09U1G10 | pH Correction Tank Agitator
09U1G11A | HRSCC Feed Pump A
09U1G11B | HRSCC Feed Pump B
09U1G12 | pHCT Agitator
09U1G13A | Centrifuge feed pump- A
09U1G13B | Centrifuge feed pump- B
09U1G14A | Bio Tower Feed Pump A
09U1G14B | Bio Tower Feed Pump B
09U1G15A | Bio Tower Recirculation - A
09U1G15B | Bio Tower Recirculation - B
09U1G16A | Air Blower 16-A
09U1G16B | Air Blower 16-B
09U1G17 | Air Blower
09U1G1A | Heat Exchanger Feed Pump-A
09U1G1B | Heat Exchanger Feed Pump-B
09U1G20 | C-MEM A Water Transfer Pump
09U1G21 | Process Water Transfer pump
09U1G22 | C-MEM B Water Transfer Pump
09U1G23 | C-MEM A Backwash Pump
09U1G24 | C-MEM B Backwash Pump
09U1G25 | RO Cartridge feed Pump
09U1G26 | RO High Pr. Pump
09U1G27 | RO Permeate Transfer Pump
09U1G28 | RO Cleaning Soln. Pump
09U1G29A | Lime Dosing Pump- A
09U1G29B | Lime Dosing Pump- B
09U1G2A | Lamella Feed Pump A
09U1G2B | Lamella Feed Pump B
09U1G3 | Flash Mixer 4A
09U1G30 | Lime Tank Agitator
09U1G32 | FeCl3Dosing Tank Agitator
09U1G35 | Polymer Dosing tank Agitator
09U1G36B | Acid Doasing Pump B
09U1G38 | Deoiling Polymer tank Agitator
09U1G39 | PAC Dosing Pump
09U1G4 | Flocculator Tank Agitator 4B
09U1G41 | Nutrient Dosing Pump
09U1G42 | Nutrient Dosing tank Agitator
09U1G43 | NaOCl Dosing Pump
09U1G44 | Organic Clining Doasing Pump
09U1G45 | Organic Clining tank Agitator
09U1G51 | Cleaning Soln. Tank Agitator
09U1G52 | Dewatering Polymer Dosing Pump
09U1G53 | Dewatering Polymer Tank Agitator
09U1G54 | NaOH Dosing Pump
09U1G55 | NaOH Tank Agitator
09U1G5A | DAF FeedPump - A
09U1G5B | DAF FeedPump - B
09U1G6 | Flash Mixer Tank Agitator 7A
09U1G7 | Flocculator Tank Agitator 7B
09U1G8 | Air compressor
09U1G9 | DAF High Pr. Pump
09U2G1A | Effluent transfer pump
10G01A | F.D.Fan
10G01B | F.D.Fan
10G01C | F.D.Fan
10G02 | Recycle H2 Compressor
10G03A | Naphtha feed pump
10G03B | Naphtha feed pump
10G04A | BWF pumps
10G04B | BWF pumps
10G05 | Naphtha condensate pump
10G15B
10U2G1 | TNP Dosing pump
10U2G2 | Na2S Dosing pump
10U2G3 | Mixer for phosphat tank
10U2G4 | Mixer for Hydrozen tank
14G01A | Alcohol feed pump
14G02A | Alcohol feed pump
14G03A | Alcohol feed pump
14P01A | Storage tank area
14P01B | Fatty acid pump-1
14P01C | Fatty acid pump-2
14P01D | Fatty acid pump-3
14P02A | Caustic unloading pump
14P02B
14P04A | Caustic unloading pump - 3
14P04B | Caustic soda transfer pump from PIT
14P05 | Slop sump pump
14P07 | caustic unloading pump
20P01 | Hot well pump
20P02A | Cold well pump
20P02B | Cold well pump
20P03A | Cooling water pump-1
20P03B | Cooling water pump-2
20P04A | Cooling water pump-3
20P05A | Cooling water pump-4
20P07A | Raw water pump-1
20P07B | Raw water pump-2
20U01A | Chilled water pump
20U03B01 | Cooling tower fan-3
20U04A01 | Cooling tower fan-1
20U04B01 | Cooling tower fan-2
20U05B01 | Blower for side stream filter
22P1A | Condensate transfer pump B
22P1B | Condensate transfer pump A
23P02
23-P1 | Effluent transfer pump
A-651A | Agitator
A-651B | Agitator
A-651C | Agitator
A-704 | Mixer
AG-7106 | BATCH BLEACHER AGITATOR
AG-7110 | ATFD STIRRER
AG-801
AG-802
AGITATOR | Agitator motor
B-150.1 | Centrifugal fan
B-250.8A | Automatic cleaning bag filter
BDG-1
BDG-2
C-103A | Recycle compressor
C-103B | Recycle compressor
C-128.1 | Washing column feed pump
C-301 | cooling water pump -1
C-302 | cooling water pump -2
C-303 | cooling water pump -3
C-401 | PUMP
C-402 | PUMP
C-403 | PUMP
C-901 | Post cooler chain conveyor
C-902 | Rotoform Ist pastillator
C-903 | Steel belt conveyor
C-904 | conveyor No 1
C-905 | conveyor No 2 (wood steeper)
C-906 | conveyor No 3(metal detector)
C-907 | Conveyer no.4(Bag rejector)
catalyst hoist motor
CH-7000A
CH-7000B
CT FAN-1 | CT FAN-1 JUTASAMA
CT FAN-2 | CT FAN-2 JUTASAMA
CT FAN-3 | CT FAN-3 K3'
CT-903A-F | Cooling tower fan
CT-903B-F | Cooling tower fan
CT-903C-F | Cooling tower fan
D-1-1 | Hotwell pump
D-117.2 | Tinipal feed tank
D-117.3 | Super fat feed pump
D-1-2 | Hotwell pump
D-150.5 | Intermediate collecting tank
D-150.6 | Intermediate collecting tank
D-201.1 | Soap feed pump
ETP Homogeneous Dosing tank agitator | ETP Homogeneous Dosing tank agitator
ETP Homogeneous tank-B motor | ETP Homogeneous tank-B motor
F/P-I | 1st Treated Sweet Water Filter Press
F/P-II | 2nd Treated Sweet Water Filter Press
F/P-III | 3rd Treated Sweet Water Filter Press
F-101 | ID fan
F-102 | FD fan
F-150.1A | Filter press for basic filteration A
F-150.1B | Filter press for basic filteration B
FD-308 | NEW FLAKER DRUM 1 MOTOR
FD-309 | NEW FLAKER DRUM 1 MOTOR
FD-310 | CONVEYOR MOTOR
FL-101 | Flaker
G11B M 01 | Dosing pump
G20 M01 | Dosing pump
IAEC boiler feed water pump-2
lindhe plant | Dosing pump-2
LP-118
P-01 | Hot well pump
P-100A1 | Naphta feed pump
P-100A2 | Naphta feed pump
P-100B1 | Naphta feed pump
P-100B2 | Naphta feed pump
P-101 | Transfer pump
P-101 | High pressure pump
P-101.6 | Hot water pump
P-101A | BFW pump
P-101B | BFW pump
P-102 | High pressure pump
P-102.1 | Hydro sulphite solution pump
P-103 | Hot oil circulation pump
P-103 | High pressure pump
P-104 | Water ring vacuum pump
P-104.1 | EDTA Dosing Pump
P-104A | Feed pump Oil to V- 101
P-104B | Feed pump Oil to V- 101
P-104C | Feed pump Jutasama
P-104D | Feed pump Jutasama
P-105 | Cooling water transfer pump
P-105A | Water Feed Pump
P-105B | Water Feed Pump
P-106A | Split Fatty Acid Transfer Pump
P-106B | Split Fatty Acid Transfer Pump
P-107A | Crude OIl CIrculation Pump
P-107B | Crude OIl CIrculation Pump
P-109 | Collected oil transfer pump
P-114B
P-117.2 | Tinopal dosing pump
P-117.3 | Superfat doasing motor
P-117.4 | Giycerine doasing pump
P-121.3A | NACI solution recycle pump
P-121.3B | NACI solution recycle pump
P-122.2 | Caustic soda transfer pump
P-124.3 | Soap transfer pump
P-124.6 | Lye transfer pump
P-124.7 | Soap transfer pump
P-128.10 | Centrifuge feed pump
P-128.12A | Soap to storage pump
P-128.12B | Soap to storage pump
P-128.15 | Soap Recycle pump
P-128.1A | Fat feed pump-1
P-128.1B | Fat feed pump-2
P-128.1C | Fat feed pump-3
P-128.2 | Brine feed pump
P-128.21 | Vaccum pump
P-128.3 | Caustic soda feed pump
P-128.5 | Nutralization agent feed pump
P-128.6A | Reactor recyle pump
P-128.6A | Seal water pump
P-128.7 | Static separator feed pump
P-128.8 | Washing column feed pump
P-128.9 | Column lye reactor pump
P-14A | E-103 thermic fluid circulation pump
P-14B | E-103 thermic fluid circulation pump
P-150.1 | Spent lye feed pump
P-150.2 | Filteration pump
P-150.3 | Mixer feed pump
P-150.4 | Filteration pump
P-150.5 | HCL acid dosing pump
P-150.6 | Coagulant dosing pump
P-150.7 | Caustic soda dosing pump
P-150.8 | Caustic soda recycle pump
P-150.9 | Feeding soap lye pump
P-168.1A | Cool(Spent lyes feed pump)
P-168.10 | Crude glycerine extraction pump
P-168.11 | Centrifugal pump for con. Rec.
P-168.1A | Vaccum filter motor 1
P-168.1B | Vaccum filter motor 1
P-168.1C | Vaccum filter motor 1
P-168.1D | Vaccum filter motor 1
P-168.2 | First effect recycle pump
P-168.2B | S/W circulation Pump
P-168.3 | Second effect recycle pump
P-168.3B | S/W circulation Pump
P-168.4 | Condensate pump
P-168.4B | S/W circulation Pump
P-168.5 | Crude glycerine extration pump
P-168.5B | Crude Gly. Transfer Pump
P-168.6 | Centrifugal pump for brine
P-168.7 | Liquid wing vaccum pump
P-168.9 | Filtrate pump from S168.1
P-180.1 | Coagulant transfer pump
P-180.1A | Coagulant transfer pump
P-180.2 | Coagulant transfer pump
P-180.4 | C.P. glycerine storage
P-200.1 | Soap filteration pump
P-201 | High Pressure Fat Feed Pump
P-201 | Forced Cooling fan for p-201
p-201A
P-202 | High Pressure Fat / Water Feed Pump
P-202 | Forced Cooling fan for p-202
P-203 | Water Charge Pump.
P-203 | Forced Cooling fan for p-203
P-203.1 | Silicate feed pump
P-205A | Water Feed Pump
P-205B | Water Feed Pump
P-206.1 | Vaccum pump
P-206.2 | Hot well pump -1
P-206.3 | Hot well pump -2
P-206A | Fatty Acid Circulation Pump
P-206B | Fatty Acid Circulation Pump
P-208A | Fat Circulation Pump
P-208B | Fat Circulation Pump
P-209 | Collected oil transfer Pump
P-2601A | Thermic fluid circulation pump
P-2601B | Thermic fluid circulation pump
P-27A | Water ring vacuum pump
p-27B | Water ring vacuum pump
P-29A | K-3 Reboiler circulation pump
P-29B | K-3 Reboiler circulation pump
P-303A | C6/C8 transfer pump-1
P-303B | C6/C8 transfer pump-2
P-304A | C10/12 transfer pump-1
P-304B | C10/12 transfer pump-2
P-305A | C8/C10 transfer pump-1
P-305B | C8/C10 transfer pump-2
P-306A | C12/C14 transfer pump-1
P-306B | C12/C14 transfer pump-2
P-307A | Reboiler circulation pump-1
P-307B | Reboiler circulation pump-2
P-308A | Reboiler circulation pump-1
P-308B | Reboiler circulation pump-2
P-309A | Bottom product transfer pump-1
P-309B | Bottom product transfer pump-2
P-30A | K-3 bottom product transferring pump
P-30B | K-3 bottom product transferring pump
P-30C | K-3 bottom product transferring pump
P-310A | Bottom product transfer pump-1
P-310B | Bottom product transfer pump-2
P-311A | Hot oil circulation pump-1
P-311B | Hot oil circulation pump-2
P-312A | Hot oil circulation pump-1
P-312B | Hot oil circulation pump-2
P-313A | Dryer circulation pump-1
P-313B | Dryer circulation pump-2
P-314A | LE transfer pump-1
P-314B | LE transfer pump-2
P-317A | SFA feed pump-1
P-317B | SFA feed pump-2
P-318A | Hot oil dooster pump-1
P-318B | Hot oil dooster pump-2
P-31A | E-13 Condensate transferring pump
P-31B | E-13 Condensate transferring pump
P-320A | Oil circulation pump-1
P-320B | Oil circulation pump-2
p-320D
P-322A | Direct CW pump-1
P-322B | Direct CW pump-2
P-323A | Effluent transfer pump
P-323B | Effluent transfer pump
p-323C
p-323D
P-324A | Condensate pump-1
P-324B | Condensate pump-2
P-326A | Cooling water pump-1
P-326B | Cooling water pump-2
P-327A | Oil transfer pump to storage tank
P-32A | M/D transferring pump
P-32B | M/D transferring pump
P-32C | M/D transferring booster pump
P-33A | E-12 thermic fluid circulation pump
P-33B | E-12 thermic fluid circulation pump
P-34A | D-20 DM water V-303
P-34B | D-20 DM water V-303
P-350A | New k3' feed
P-350B | New k3' feed
P-351A | Dehydrator circulation Pump
P-351B | Dehydrator circulation Pump
P-352A | L/E Transfer Pump of Dehydrator
P-352B | L/E Transfer Pump of Dehydrator
P-353A | Hot oil circulation Pump (preheater)
P-353B | Hot oil circulation Pump (preheater)
P-354A | Bottom recirculation pump
P-354B | Bottom recirculation pump
P-355A | B/P Pump K3'
P-355B | B/P Pump K3'
P-356A | Hot oil circulation Pump (reboiler)
P-356B | Hot oil circulation Pump (reboiler)
P-357A | Pump around system pump
P-357B | Pump around system pump
P-358A | L/E Transfer Pump of C-303
P-358B | L/E Transfer Pump of C-303
P-359A | Side draw transfer pump of C-303
P-359B | Side draw transfer pump of C-303
P-360A | Hotwell Pump
P-360B | Hotwell Pump
P-361A | Tempered water pump
P-361B | Tempered water pump
P-362A | Cooling water pump-K3'
P-362B | Cooling water pump-K3'
P-362C | Cooling water pump-Jutasama
P-362D | Cooling water pump-Jutasama
P-363A | DM water pump
P-363B | DM water pump
P-364A | Clean CW Pump -Precon & Postcon
P-364B | Clean CW Pump -Precon & Postcon
P-365A | Dirty Water Pump
P-365B | Dirty Water Pump
P-36A | K-3 Reboiler thermic fluid circulation pump
P-36B | K-3 Reboiler thermic fluid circulation pump
P-3A | Feed pump to D-10
P-3B | Feed pump to D-10
P-402A | LE transfer pump-1
P-402B | LE transfer pump-2
P-407A | Residue transfer pump-1
P-407B | Residue transfer pump-2
P-409A | LE transfer pump fromV-403-1
P-409B | LE transfer pump fromV-403-2
P-410A | Bottom circulation pump for C-402-1
P-410B | Bottom circulation pump for C-402-2
P-411A | Hot oil transfer pump for ER-402-1
P-411B | Hot oil transfer pump for ER-402-2
P-412A | Distillate transfer pump-1
P-412B | Distillate transfer pump-2
P-414A | HFA transfer pump-1
P-414B | HFA transfer pump-2
P-418A | Hot oil booster pump-1
P-418B | Hot oil booster pump-2
P-419A | SFA feed pump-1
P-419B | SFA feed pump-2
p-419C
P-420A | Hot oil transfer pump -1
P-420B | Hot oil transfer pump -2
P-421A | L/E transfer pump
P-421B | L/E transfer pump
P-422A | Direct cooling water return pump-1
P-422B | Direct cooling water return pump-2
p-422C | Thermic fluid pump
P-422D | Thermic fluid pump
P-423B
P-423C
P-423D | Column 401 reboiler circulation pump
p-424A
P-424B
P-426A | Internal Circulation Pump
P-426B | Internal Circulation Pump
P-430A | ICW circulation pump-1
P-430B | ICW circulation pump-2
P-430C | ICW circulation pump-3
P-431A | Dryer Circulation Pump
P-431B | Dryer Circulation Pump
P-450A | New SPD feed
P-450B | New SPD feed
P-451A | Motor For Dehydrator Pump P-451A
P-451B | Motor For Dehydrator Pump P-451B
P-452A | Motor For Steam Separator P-452A
P-452B | Motor For Steam Separator P-452B
P-453A | Motor For Thermic Fluid Circulation preheater P-453A
P-453B | Motor For Thermic Fluid Circulation preheater P-453B
P-454A | Motor For SPD main distillate P-454A
P-454B | Motor For SPD main distillate P-454B
P-455A | Motor For SPD Bottom P-455A
P-455B | Motor For SPD Bottom P-455B
P-456A | Motor For Hot well Circulation P-456A
P-456B | Motor For Hot well Circulation P-456A
P-457A | Motor For Thermic Fluid water Circulation Reboiler P-457A
P-457B | Motor For Thermic Fluid water Circulation Reboiler P-457B
P-4A | D-10 to K-3
P-4B | D-10 to K-3
p-510A
P-511A | Bottom circulation pump
P-511B | Bottom circulation pump
P-512A | Bottom draw pump
P-512B | Bottom draw pump
P-513A | Hot oil circulation pump
P-513B | Hot oil circulation pump
P-514A | Distillate transfer pump
P-514B | Distillate transfer pump
P-515A | Pump for steam generator
P-515B | Pump for steam generator
P-516A | Light end transfer pump
P-516B | Light end transfer pump
P-517A | SPD Distilate Transfer Pump
P-517B | SPD Distilate Transfer Pump
P-518A | SPD Distilate Residue Transfer Pump
P-518B | SPD Distilate Residue Transfer Pump
p-518C
P-519A | Thermic fluid pump
P-519B | Thermic fluid pump
P-520 | Feed pump for SPD
P-522 | Vaccum pump
P-523 | Feed pump
p-551B
P-602A | High Pressure Fat / Water Feed Pump
P-602B | High Pressure Fat / Water Feed Pump
P-604A | Crude Sweet Water Transfer Pump
P-604B | Crude Sweet Water Transfer Pump
P-604C | CRUDE SWEET WATER TRANSFER PUMP
P-605 | Decanted oil transfer pump
P-606 | Fatty Acid Circulation Pump
P-607 | Fat Circulation Pump
P-608 | Fat Circulation Pump
P-610 | Skimmed oil transfer pump
P-651A | Feed Pump
P-651A | Product x'per pump
P-651B | Feed Pump
P-652 | Transfer/Recirculation
P-652A | Hot water x'per pump-1
P-652B | Hot water x'per pump-2
P-653 | Transfer/Recirculation
P-653A
P-653B | C.W.R.Pump(Pastillator Ground Floor)
P-654 | Transfer/Recirculation
P-655 | Product Pump
P-656A | Condensate Pump
P-656B | Condensate Pump
P-657A | Condensate Pump
P-657B | Condensate Pump
P-658 | pump nr to p-9002A
P-685 | Hot Oil Pump
P-686 | Crude Glycerin Transfer pump
P-687 | Hot Well pump
P-688 | Sweet water hot well pump
P-689 | Precon Sweet water pump
P-702 A | vessel 702 bottom circulation pump
P-702B | vessel 702 bottom circulation pump
p-703A/B
P-704A | Finish Material Tr. Pump
P-704B | Finish Material Tr. Pump
P-705 | Circulation Pump
P-706A | D.M. Water Pump
P-706B | D.M. Water Pump
P-707B
P-7100A | TANK FORM FEED PUMP
P-7100B | TANK FORM FEED PUMP
P-7101 | CRUDE RECIRCULATION PUMP
P-7102 | DEODERIZER DRYER RECIRCULATION PUMP
P-7103A | FEED PUMP
p-7103B | FEED PUMP
P-7104A | RESIDUE TRANSFER PUMP
P-7104B | RESIDUE TRANSFER PUMP
P-7106 | DISTILLATE PUMP
P-7107 | BLEACHER FEED PUMP
P-7108 | SUB STANDARD GLYCERINE TRANSFER PUMP
P-710A | Vaccum Pump
P-710B | Vaccum Pump
P-7110A | PITCH PUMP
P-7110B | PITCH PUMP
P-7111 | INTERMEDIATE DISTILLED GLYCERINE X-MER PUMP
P-7112 | FLASH VESSEL-II
P-7113 | X-FER PUMP FROM ATFD RECEIVER
P-7114A | X-FER PUMP FROM HOT WELL TO COOLING WATER
P-7114B | X-FER PUMP FROM HOT WELL TO COOLING WATER
P-7115A | COOLING TOWER X-FER PUMP-1
P-7115B | COOLING TOWER X-FER PUMP-2
p-7117 | INTERMEDIATE REFINED GLYCERINE X-FER PUMP
p-7118 | FIRST STAGE FLASH PUMP
P-7119 | SECOND STAGE FLASH PUMP
P-711A | Loop-1
P-711B | Loop-2
P-711C | Loop-3
P-7120 | ATFD FEED PUMP
P-7121 | SCRUBBER CIRCULATION PUMP
P-7122
p-7123 | HOT OIL X-FER PUMP FOR E-102
P-7124 | HOT OIL FOR ATFD
P-7125 | SCRUBBER DISCHARGE PUMP
P-7126A | SCRUBBER CIRCULATION PUMP
P-7126B | SCRUBBER CIRCULATION PUMP
P-7126C | SCRUBBER CIRCULATION PUMP
P-7126D | SCRUBBER CIRCULATION PUMP
P-7127A | FINISHED GOOD LOADING PUMP
P-7127B | FINISHED GOOD LOADING PUMP
P-7128 | PIT PUMP
P-755B
P-757A
P-765 | Bottom circulation pump
P-795 | Vaccum Pump
P-8001A | Condensate Transfer Pump
P-8001B | Condensate Transfer Pump
P-801A | Trolly Unloading Pump-1
P-801B | Trolly Unloading Pump-2
P-801C | TROLLY UNLOADING PUMP-3
P-801D | TROLLY UNLOADING PUMP-4
P-801E | TROLLY UNLOADING PUMP-5
P-801F | TROLLY UNLOADING PUMP-6
P-802A | Crude oil transfer pump-1
P-802B | Crude oil transfer pump-2
P-802C | Crude oil transfer pump-3
P-802C | Crude oil transfer pump-3
P-803 | FEED PUMP
P-804A | Feed for C-301/302
P-804B | Feed for C-301/302
P-806A | C12 LAURIC/PKD unloading pump-1
P-806B | C12 LAURIC/PKD unloading pump-2
P-807A | C12 LAURIC/PKD transfer pump-1
P-807B | C12 LAURIC/PKD transfer pump-2
P-808A | Old K3/k4 feed
P-808B | Old K3/k4 feed
P-809 | Feed alcohol
P-811A | 401/402 Feed pump
P-811B | 401/402 Feed pump
P-812B | Distilled FPAD/CPS transfer pump
P-813A | Heavy end transfer pump-1
P-813B | Heavy end transfer pump-2
P-815 | Glycerine transfer pump
P-816A | Oil fat trap pump
P-816B | Oil fat trap pump
P-817A | Old K3/k4 feed
P-817B | Old K3/k4 feed
P-818 | ISO LOADING PUMP
P-819A | Feed for splitting/lurgi
P-819B | Feed for splitting/lurgi
P-820 | Oil dhakka circulation pump
P-820 | Loading Unloading pump
P-821 | Loading Unloading pump
P-821A | Oil dhakka circulation pump
P-821B | Oil dhakka circulation pump
P-822A | Alcohol feed
P-822B | Alcohol feed
P-823 | Oil dhakka circulation pump
P-824 | Oil dhakka circulation pump
P-825A | Bleacher
P-825B | Bleacher
P-825C | Bleacher
P-825D | Bleacher
P-826 | Drum filling
P-827 | Oil dhakka circulation pump
P-828 | Oil dhakka circulation pump
P-829 | Oil dhakka circulation pump
P-830A | Old K3 feed
P-830B | Old K3 feed
P-831 | Vent condensate xfer pump
P-832 | Pump for settling tank
p-833
P-9002A | CW supply Pump for Splitting & SW
P-9002B | CW supply Pump for Splitting & SW
P-901A | Tempered water pump
P-901B | Tempered water pump
P-903A | Indirect cooling water pump-1
P-903B | Indirect cooling water pump-2
P-903C | Indirect cooling water pump-3
P-903D | Indirect cooling water pump-4
P-905A | Fo transfer pump
P-905B | Fo transfer pump
P-906A | RW transfer pump
P-906B | RW transfer pump
P-906C | RW transfer pump
P-908 | D.M.Water transfer pump
P-909 | Intermediate pump for mp boiler
P-910A | Cooling water return pump
P-910B | Cooling water return pump
P-913 | WTP Pump-1
P-913 | WTP Pump-1
P-914 | Filtered water booster pump
P-919A | D.M.Water transfer pump-1
P-919B | D.M.Water transfer pump-2
P-920 | Blowdown transfer pump
P-951A | Chilling water transfer pump-1
P-952A | Chilling water transfer pump-2
P-953A | Chilled water secondry Pump
P-953B | CHW secondary stnd by pump for P953A
P-954A | Chiller compressor
P-955
P-961
P-962
P-963
P-964
P-965
P-966
P-967A
P-967B
P-CD100 | Clean condensate Pump
PL-204.1 | Twin warn simplex refiner
PS-102.1 | Hydro sulphite solution pump
PS-104.1 | EDTA solution mixer
PS-168.1 | Salt dessalving mixer
R-101 | Reactor Agitator
R-102 | Bleacher Agitator
R-128.2 | Terbo disperser pump
S-128.2A | Centrifugal separator
S-128.2B | Centrifugal separator
S-128.2B | Soap mixer
S-128.2C | Centrifugal separator
S-509 | Stirrer for SPD
S-D204.1 | Vaccum sprey chamber
SPD450 | Motor For Agitator SP-D450
T-150.1A | Talc system
T-150.1B | Talc system
T-205.1 | Soap fins warm conveyor
T-205.1A | Soap fine warm conveyor
T-205.2 | Soap fins warm conveyor
T-205.2A | Soap fins warm conveyor
TF-12A | Feed for C-401/402
TF-12B | Feed for C-401/402
TF-33A | LOOP FEED PUMP
TF-33B | Feed for C-301/303
TF4-32A | FEED TO FLAKER-1
TF4-32B | FEED TO FLAKER-2
TF4-32C | FEED TO FLAKER-3
T-SC02 | Talc Screw Conveyer
V-101 | Charger Agitator
VP-27 B | NEW VP NEAR VP-27,K3
VP-351A | Vac. Pump
VP-351B | Vac. Pump
VP-451 | Motor For Vaccum Pump VP-451
VP-651A | Vacuum Pump
VP-651B | Vacuum Pump
VP-7103A | VACCUM PUMP-1
VP-7103B | VACCUM PUMP-2
VPX-601A | Water ring vacuum pump
VPX-601b | Water ring vacuum pump
VP-X-689 | Vacuum pump
X-101A | vacuum Pumps (Water Ring)
X-101B | VACUUM PUMP
X-201 | VacuumPump
X-301-1 | Vaccum pump
X-401-1 | Vaccum pump-1
X-401-2 | Vaccum pump-2
Belt converyor
CROSS TRAVEL
CROSS TRAVEL
Glvcrin Pump
Scew conveyor
Vaccum pump
HOIST 1
Buckhardt Compressor
De-watering pump Weigh-Bridge
De-watering pump tankfarm area
HOIST 2
De-watering pump main plant
Filter Press Moter A
Filter Press Moter B
HRSCC Recirculation
HRSCC Scapper
Rotadal TPI Oil Remover Pump
Condensate Transfer Pump
ATLAS Cpco comp. fan motor
Thermic Fluid F.D.Fan
Ring main pump-1
Ring main pump-2
Chemical dosing pump
Chemical tank Agitator motor
Thermic fluid transfer pump
Oil pump no.1
Oil pump no.2
De-watering pump hot oil
ETP To Cooling Tower Tr. Pump
Agitator - 1
back ceiling CONVER BELT NO-1
Sewing Head Motor
INFEED MOTEF
back ceiling CONVER BELT NO-2
Sewing Head Motor
INFEED MOTEF
TF-3/AGITATOR-MOTOR
Agitator - 2
conveyor-2
Blower
cold well pump
chiller
new flaker drum-1
conveyor-1
new flaker blower
conveyor-3 (1st floor)
Sealing machine
Lifting belt conveyor
HOT WELL PUMP
Hydralic motor
new flaker drum-2
Sealing Belt Motor
Sewing Head Motor
AHU Motor (1st Floor Pastillator)
Fridge fan blower
Blower
Guttar Pump
Feed Pump flacker
New Flakar C.W.R.Pump
VAPOUR BOILER - 1
VAPOUR BOILER - 2
BELT CONVEYOR PAST.GROUND FLR
STEEL BELT CONVEYOR BLOWER
K3 CT fan
Extract Pump
oil remover motor
Water recycle pump
AGITATOR-1 NEAR TANK-824
AGITATOR NEAR TANK-803
New Flakar Drum Motor
AGITATOR-1 NEAR TANK-821
03G16A
03G18A
03G18B
P-1000 | FAF BLOWER
P-1001A | AUX.AIR FAN A
P-1001B | AUX.AIR FAN B
P-1002 | AUX.AIR FAN 1
P-1003 | GULLOTINE DAMPER G5_01
P-1004 | GULLOTINE DAMPER G5_02
P-1005 | GULLOTINE DAMPER G5_03
P-1006 | SAF GD-01
P-1007 | SAF GD-02
P-1008 | SAF GD-03
P-1009 | SAF FD-01
P-1010A | BOILER FEED WATER PUMP-A
P-1010B | BOILER FEED WATER PUMP-B
P-1011A | THERMIC FLUID PUMP-A
P-1011B | THERMIC FLUID PUMP-B
P-1012A | COOLING WATER PUMP-A
P-1012B | COOLING WATER PUMP-B
P-1012C | COOLING WATER PUMP-C
P-1013A | CHILLED WATER PUMP-A
P-1013B | CHILLED WATER PUMP-B
P-1013C | CHILLED WATER PUMP-C
P-1014A | STARTUP VENT S24
P-1014B | STEAM SUPPLY S25
P-1015A | HOT WATER PUMP-A
P-1015B | HOT WATER PUMP-2
P-1016A | CT FAN-1
P-1016B | CT FAN-2
P-1017A | COOLING WATER GT PUMP-A
P-1017B | COOLING WATER GT PUMP-B
P-1018A | AIR COMPRESSOR-A
P-1018B | AIR COMPRESSOR-B
P-1019A | LP DOSING PUMP-A
P-1019B | LP DOSING PUMP-B
P-1019C | LP DOSING AGITATOR
P-1020A | HP DOSING PUMP-A
P-1020B | HP DOSING PUMP-B
P-1020C | HP DOSING AGITATOR
P-1021 | MAKEUP WATER PUMP
VAM-1 | VAM-1
VAM-2 | VAM-2
P-1022 | CONDENSATE TRANSFER PUMP
Pit-Pump-1
Pit pump-2
P-1023 | HOT WATER PESTILLATOR -1
P-1024 | HOT WATER PESTILLATOR -2
101.7 | Dirty cooling water return pump
P-1302 | Chilled water Pump
P 117.5 | Alcohol Transfer Pump
PLD 1301 | Plodder
P 128.2 | Condensate Transfer Pump
P 118.5 | Alc Transfer pump
VP 1301A | Vaccum Pump
VP 1301B | Vaccum Pump
CD-1301 | Chilled Drum
Conveyer Blet
Hydrolic Pack
MS 1307 | Multi Screw
BL 1301 | Blower
PSC 1301 | Scrubber Circulation Pump
P-T-1301 | Ester Vessel Transfer Pump
P-T-1302 | Sulphonification vessel
T 1301 | Esterification vessel
T 1302 | Sulphonification vessel
T 1304 A | Turbo Mixer 1
T 1304 B | Turbo Mixer 1
Note on A399: NOT IN USE
Note on A400: NOT IN USE
Note on A401: NOT IN USE
Note on A402: NOT IN USE

## Inst
| CM PLAN & COMPLETED | PM PLAN & COMPLETED
April'2016 | 88 | 185
May'2016 | 85 | 212
June'2016 | 81 | 250
July'2016 | 146 | 158
August'2016 | 175 | 172
Sept'2016 | 117 | 144
Oct'2016 | 112 | 165
Nov'2016 | 124 | 223
Dec'2016 | 112 | 246
Jan'2017 | 127 | 217
Feb'2017 | 49 | 258
March'2017 | 40 | 233
| 1256 | 2463
100%