## Sheet1
Sn | Panel Name | Equipment | Feeder | Problem | TEMP | Remark
| 1 | ACB | O2G1 Bypass Breaker | R PH O/G JAW | 96 | tightness done in shutdown by more
| 2 |  | 02G1 I/C | Y & R PH I/C | 56 | tightness done in shutdown by more
| 3 |  | 02G1 O/G CABLE | R PH O/G CABLE | 80 | tightness done in shutdown by more
| 4 |  |  | Y PH O/G CABLE | 70 | tightness done in shutdown by more
| 5 |  | INCOMER-1 | R PH I/C | 108 | tightness done in shutdown by more
| 6 |  |  | Y PH I/C | 116 | tightness done in shutdown by more
| 7 |  |  | B PH I/C | 111 | tightness done in shutdown by more
| 8 |  |  | B PH O/G | 106 | tightness done in shutdown by more
| 9 |  |  | Y PH O/G | 114 | tightness done in shutdown by more
| 10 |  |  | R PH O/G | 116 | tightness done in shutdown by more
| 11 |  | INCOMER-2 | R PH I/C | 96 | tightness done in shutdown by more
| 12 |  |  | Y PH I/C | 100 | tightness done in shutdown by more
| 13 |  |  | B PH I/C | 95 | tightness done in shutdown by more
| 14 |  |  | B PH O/G | 104 | tightness done in shutdown by more
| 15 |  |  | Y PH O/G | 109 | tightness done in shutdown by more
| 16 |  |  | R PH O/G | 105 | tightness done in shutdown by more
| 17 |  | 06G1A | O/G B PH SFU | 89 | tightness done SAL
| 18 |  | 01G7B | O/G CABLE LUG Y & B | 80
| 19 |  | B/C-2 | R PH I/C | 88 | found normal
| 20 |  |  | Y PH I/C | 80 | found normal
| 21 |  |  | B PH I/C | 80 | found normal
| 22 |  |  | B PH O/G | 80 | found normal
| 23 |  |  | R PH O/G | 87 | found normal
| 24 |  |  | Y PH O/G | 87 | found normal
| 25 |  | UMCC ACB 2 | Y PH I/C | 74
| 26 |  | 02G3 ACB | B PH I/C | 106 | Cleaned
| 27 |  |  | Y PH O/G | 64
| 28 |  | 06G1D SFU | Y PH I/C | 73 | tightness done SAL
| 29 |  | 37R4 SFU | R PH I/C | 100
| 30 |  |  | Y PH I/C | 99
| 31 |  |  | B PH I/C | 76
| 32 |  |  | R PH O/G | 81
| 33 |  |  | Y PH O/G | 82
| 34 |  |  | B PH O/G | 92
| 35 |  | EMCC MAIN ISOLATOR | R PH I/C | 61
| 36 | 3F1 | 01G3A | CONTACTOR O/G Y | 72
| 37 |  | 01G16A | O/G R PH | 78
| 38 |  | 01G14A SFU | Y PH O/G JAW | 66
| 39 | 21F4 | SFU | Y PH I/C | 56
| 40 | 17R3 | SFU | O/G R PH | 70
| 41 |  |  | O/G CABLE B PH | 62
| 42 | APFC-1 | 3F1 SFU | I/C Y PH | 205 | sfu replaced
| 43 |  | 3F3 | I/C R PH | 95 | sfu replaced
| 44 | APFC -2 | 2R5 | SFU FUSE I/C & O/G Y PH | 82
| 45 | APFC -3 | 2F1 | SFU I/C & O/G R ,Y FUSE | 72
| 46 |  | 2F2 | R & Y FUSE BODY | 70
| 47 |  | 2F3 | R & Y FUSE BODY | 72
| 48 | APFC -2 | 2F1 | I/C & O/G R ,Y FUSE | 75
| 49 |  | 2F2 | I/C & O/G R ,Y FUSE | 72
| 50 |  | 2R3 | O/G OF B PH | 72
| 51 | 02G1A VFD |  | RESI ABOVE CONTACTOR | 124 | ok
| 52 |  |  | RESI BELOW CONTACTOR | 110 | ok
| 53 | 02G5B |  | Y SFU I/C B PH LUG | 80
| 54 | NEW PMCC | 1R1 ACB | R PH I/C | 134
| 55 |  |  | Y PH I/C | 105
| 56 |  |  | B PH I/C | 102
| 57 | NEW PMCC | APFC-1 | R PH O/G | 130 | both breaker jaw replaced
| 58 |  |  | Y PH O/G | 107 | both breaker jaw replaced
| 59 |  |  | B PH O/G | 106 | both breaker jaw replaced
| 60 | NEW PMCC | 02G1A ACB | R PH O/G | 69
| 61 | NEW PMCC | CPP ACB 8R2 | R PH I/C | 93
| 62 |  |  | Y PH I/C | 88
| 63 |  |  | R PH O/G | 93
| 64 | NEW PMCC | APFC-1 PANEL MAIN ACB | R PH I/C | 110 | breaker moving contact replaced under observation
| 65 |  |  | Y PH I/C | 116 | breaker moving contact replaced under observation
| 66 |  |  | B PH I/C | 108 | breaker moving contact replaced under observation
| 67 |  |  | R PH O/G | 119 | breaker moving contact replaced under observation
| 68 |  |  | Y PH O/G | 114 | breaker moving contact replaced under observation
| 69 |  |  | B PH O/G | 120 | breaker moving contact replaced under observation
| 70 | NEW PMCC | 5TH HARMONIC ACB | R PH I/C | 82
| 71 | NEW PMCC | 7TH HARMONIC SFU | Y PH I/C | 63
| 72 | NEW PMCC | APFC -2 MAIN ACB | B PH O/G | 66
| 73 | NEW PMCC | CHP ACB O/G | R PH I/C | 79
| 74 |  |  | Y PH I/C | 74
| 75 |  |  | B PH I/C | 78
| 76 | PESTILLATOR | P-962 | R PH O/G | 67 | REPLACED LUG
| 77 | PESTILLATOR | P-967B | O/G CABLE LUG B2 | 64 | REPLACED LUG
| 78 | CHP | VFD PANEL ACB | Y PH I/C | 76 | tightness done during shutdown 29.6.16
| 79 |  |  | Y PH O/G | 74 | tightness done during shutdown 29.6.16
| 80 | CHP PMCC | MAIN ACB | R PH O/G | 60 | tightness done during shutdown 29.6.16
| 81 |  |  | Y PH O/G | 76 | tightness done during shutdown 29.6.16
| 82 |  |  | B PH O/G | 72 | tightness done during shutdown 29.6.16
| 83 | CHP PMCC | VFD ACB O/G FDR | R PH I/C | 60 | tightness done during shutdown 29.6.16
| 84 |  |  | Y PH I/C | 95 | tightness done during shutdown 29.6.16
| 85 |  |  | B PH I/C | 80 | tightness done during shutdown 29.6.16
| 86 |  |  | R PH O/G | 67 | tightness done during shutdown 29.6.16
| 87 |  |  | Y PH O/G | 75 | tightness done during shutdown 29.6.16
| 88 |  |  | B PH O/G | 92 | tightness done during shutdown 29.6.16
| 89 | CPP | CPP PMCC MAIN ACB | Y PH I/C | 71
| 90 | CPP | P-1010A RELAY | R PH I/C | 85
| 91 |  |  | Y PH I/C | 82
| 92 |  |  | B PH I/C | 60
| 93 | CPP | P-1010A MAIN CONT | R PH O/G | 96
| 94 | GDP | GDP MCC MCCB | R PH I/C | 74
| 95 |  |  | Y PH I/C | 73
| 96 |  |  | B PH I/C | 66
| 97 |  |  | R PH O/G | 83
| 98 |  |  | Y PH O/G | 80
| 99 |  |  | B PH O/G | 76
| 100 |  | 06G1D SFU COMP HOUSE | R PH I/C | 165 | relugging done
| 101 |  |  | Y PH I/C | 117 | relugging done
| 102 |  |  | B PH I/C | 79
| 103 |  | 05G9A SFU | R PH I/C | 72
| 104 |  |  | Y PH I/C | 76
| 105 |  |  | B PH I/C | 69
| 106 |  |  | R PH O/G | 110 | FUSE CONTACT
| 107 |  |  | Y PH O/G | 62
| 108 |  |  | B PH O/G | 92 | FUSE CONTACT
| 109 |  | 05G9C SFU | R PH I/C | 87 | FUSE CONTACT
| 110 |  |  | Y PH I/C | 94 | FUSE CONTACT
| 111 |  |  | B PH I/C | 108 | FUSE CONTACT
| 112 |  |  | R PH O/G | 72 | FUSE CONTACT
| 113 |  |  | Y PH O/G | 84 | FUSE CONTACT
| 114 |  |  | B PH O/G | 96 | FUSE CONTACT
| 115 |  | K3 PANEL MCCB | R PH I/C | 64
| 116 |  |  | Y PH I/C | 61
| 117 |  |  | B PH I/C | 57
| 118 |  |  | R PH O/G | 58
| 119 |  |  | Y PH O/G | 53
| 120 |  |  | B PH O/G | 53
| 121 |  | MCC D2 PANEL ACB | R PH I/C | 53
| 122 |  |  | Y PH I/C | 46
| 123 |  |  | B PH I/C | 46
| 124 |  |  | R PH O/G | 43
| 125 |  |  | Y PH O/G | 43
| 126 |  |  | B PH O/G | 44
| 127 | MCC 103 | P-407A | R O/G CABLE LUG | 83
| 128 | JUTASAMA | UMCC PANEL ACB | R PH O/G | 47
| 129 |  |  | Y PH O/G | 60
| 130 |  |  | B PH O/G | 50
| 131 | SAP UMCC | 20P03B SFU | R PH I/C | 108 | Cleaned
| 132 |  |  | Y PH I/C | 107 | Cleaned
| 133 |  |  | B PH I/C | 92 | Cleaned
| 134 |  |  | R PH O/G | 103 | Cleaned
| 135 |  |  | Y PH O/G | 112 | Cleaned
| 136 |  |  | B PH O/G | 96 | Cleaned
| 137 | SAP UMCC 4R3 | 20P07B | R PH O/G CU LINK LUG | 72
| 138 | APFC-1B | 2F2 | SFU /G Y PH | 72
| 139 |  |  | R PH O/G LUG | 74
| 140 | PCC 3F1 | APFC-1 ACB | R PH O/G | 74
| 141 |  |  | Y PH O/G | 81
| 142 |  |  | B PH O/G | 75
| 143 | DFA PCC | I/C-1 | R PH I/C | 64
| 144 |  |  | Y PH I/C | 86
| 145 |  |  | B PH I/C | 56
| 146 |  |  | R PH O/G | 58
| 147 |  |  | Y PH O/G | 75
| 148 |  |  | B PH O/G | 72
| 149 | PCC 8R1 | APFC-2 ACB | R PH O/G | 76
| 150 |  |  | Y PH O/G | 62
| 151 |  |  | B PH O/G | 60
| 152 | DFA PCC | I/C-2 ACB | R PH I/C | 74
| 153 |  |  | Y PH I/C | 73
| 154 |  |  | B PH I/C | 70
| 155 |  |  | R PH O/G | 54
| 156 |  |  | Y PH O/G | 80
| 157 |  |  | B PH O/G | 69
| 158 | DFA PCC | MCC 103 1FA3 | R PH I/C | 78
| 159 |  |  | R PH O/G | 50
| 160 |  |  | B PH O/G | 78
| 161 | DFA PCC | K3 MCC 14F3 SFU | B PH O/G | 85
| 162 | APFC-1 PANEL | 3F3 SFU FUSE CONTACT | Y PH O/G | 82
| 163 | APFC-1 PANEL | 3F4 SFU FUSE CONTACT | R PH I/C | 171 | Cleaned
| 164 |  |  | Y PH I/C | 106 | Cleaned
| 165 |  |  | B PH I/C | 80
| 166 |  |  | R PH O/G | 105 | Cleaned
| 167 |  |  | Y PH O/G | 101 | Cleaned
| 168 |  |  | B PH O/G | 82
| 169 | APFC-2 PANEL | 2R1 O/G CU LINK LUG | B PH O/G | 97
| 170 | APFC-2 PANEL | MAIN ACB | R PH O/G | 74
| 171 |  |  | Y PH O/G | 71
| 172 |  |  | B PH O/G | 84
| 173 | DFA APFC-1 | MAIN ACB | R PH I/C | 56
| 174 |  |  | Y PH I/C | 65
| 175 |  |  | B PH I/C | 61
| 176 |  |  | R PH O/G | 60
| 177 |  |  | Y PH O/G | 64
| 178 |  |  | B PH O/G | 62
| 179 | NEW FLKR MCC | C-301 | B PH O/G | 110 | done by Bhimpatil 24.6.16
| 180 |  |  | Y PH O/G | 96 | done by Bhimpatil 24.6.16

## Sheet2
Sn | Panel Name | Equipment | Feeder | Priority | Page Number | Image no | Problem | TEMP | Remark
1 |  | 1000A ACB | O2G1 Bypass Breaker | 3 | 3 | 17013 to 17018 |  |  | need to check the termination
2 |  | O/G Cable Termination | Inline Pump for O1E3 | 3 | 7 | 17034 | O/G cable Y lug temp 74.7 others 57 to 60 |  | need to check the termination
3 |  | 4000A ACB | Transformer I/C - 2 | 3 | 7,8 | 17035 to 17040 |  |  | need to check the termination
4 |  | 2500A ACB | Buscoupler - 2 | 3 | 9 | 17042 to 17045 |  |  | need to check the termination
5 |  | SFU 250A Termination | I/C EMCC 37R4 | 3 | 12,13 | 17057 to 17062 | Y Fuse jaw temp 100 |  | need to check the termination
6 |  | MNX 110A Contactor | O/G 01G16A | 3 | 15 |  |  |  | need to check the termination
7 |  | SFU 125A | APFC 2F3 | 3 | 19 |  |  |  | need to check the termination
8 |  | ACB 1250A | New PMCC 1R1 | 3 | 26 |  |  |  | need to check the termination
9 |  | ACB 1600A | New PMCC 8R2 CPP | 3 | 28 |  |  |  | need to check the termination
10 |  | 1250A ACB | APFC 1 | 3 | 29 |  |  |  | need to check the termination
11 |  | SFU 250A | O6G1D Field Side | 3 | 38 |  |  |  | need to check the termination
12 |  | SFU 200A | 20PU3B UMCC | 3 | 43 |  |  |  | need to check the termination
13 |  | L&T 4000A ACB | PCC I/C 2 ACB | 3 | 49 |  |  |  | need to check the termination
14 |  | SFU 630A | K3 MCC PCC panel | 3 | 51 |  |  |  | need to check the termination
15 |  | SFU 125A | APFC 1 3F4 | 3 | 52 |  |  |  | need to check the termination
16 |  | SFU 200A | APFC 1R1 | 3 | 53 |  |  |  | need to check the termination