## losses attained
Sr No | Description | Floor | Location | Impact | Steam pressure | No of leakages | bore size | Steam loss | Steam rate | Loss per month | Loss per Annum | Status
[5 empty] | (BarG) | Nos | mm | (KG/hr) | (Rs/kg) | Rs/month | Lacs/annum
INSTRUMENT
1 | FT-753 & FT-754 showing wrong reading | [10 empty] | Attained
UTILITY
1 | HP line steam traps are pass (3 nos) | ground floor | between DFA & FAP | HP Steam loss | 60 | 3 | 1.5 | 55.97 | 1.67 | 201894.984 | 22.2084 | Attained
2 | HP steam header trap pass and valve leak | ground floor | utility building | HP Steam loss | 60 | 2 | 1 | 24.87 | 1.67 | 59807.376 | 6.5788 | Attained
3 | MP steam header trap pass | ground floor | near IAEC | MP Steam loss | 12 | 1 | 3 | 42.13 | 1.67 | 50657.112 | 5.5723 | Attained
4 | MP steam line valve pass | 1st floor | utility building | MP Steam loss | 12 | 1 | 1 | 18.72 | 1.67 | 22508.928 | 2.476 | Attained
DFA
1 | tracing line flange leak (2 nos) | 1/2th floor | JST building | LP steam loss | 3 | 2 | 2 | 5.81 | 1.67 | 13971.888 | 1.5369
2 | tracing line flange leak (1 nos) | 1st floor | JST building | LP steam loss | 3 | 1 | 2 | 5.81 | 1.67 | 6985.944 | 0.76845
3 | tracing line flange leak (1 nos) | 3rd floor | on E-359 | LP steam loss | 3 | 1 | 2 | 5.81 | 1.67 | 6985.944 | 0.76845
4 | tracing line flange leak (1 nos) | 4th floor | near D-10 | LP steam loss | 3 | 1 | 2 | 5.81 | 1.67 | 6985.944 | 0.76845
5 | Steam trap pass of Sec-5 vacuum system (2 nos) | 5th floor | DFA | MP steam loss | 12 | 2 | 2 | 18.72 | 1.67 | 45017.856 | 4.952 | Attained
6 | tracing line flange leak (1 nos) | 5th floor | New SPD bottom | LP steam loss | 3 | 1 | 2 | 5.81 | 1.67 | 6985.944 | 0.76845
7 | tracing line flange leak (6 nos) | 6th floor | near P-357 | LP steam loss | 3 | 6 | 2 | 5.81 | 1.67 | 41915.664 | 4.6107
8 | tracing line flange leak (2 nos) | 6th floor | near V-101 | LP steam loss | 3 | 2 | 2 | 5.81 | 1.67 | 13971.888 | 1.5369
9 | tracing line flange leak (2 nos) and Valve leak(2 nos) | 7th floor | nearC301/302 vacuum system | MP Steam loss | 12 | 2 | 2 | 18.72 | 1.67 | 45017.856 | 4.952 | Attained
10 | 1/2" steam valve open (30%) | 6th floor | C-303 vacuum system | MP Steam loss | 10 | 1 | 2 | 15.82 | 1.67 | 19021.968 | 2.0924 | Attained
11 | E-365 unisulated | 7th floor | E-365 | Heat loss | [6 empty] | 1.65 | Attained
12 | E-366 unisulated | 8th floor | E-366 | Heat loss | [6 empty] | 1.98 | Attained
13 | JST/C-303 CT fills are randomly filled in CT | Top floor | DFA
14 | Alpha laval CT fills are choked | Top floor | DFA | Fills are randomly installed, results in decrease in efficiency of Cooling tower
15 | Rain water collected on top floor . | Top floor |  | Algae formation on floor | [7 empty] | Attained
16 | Pump 20P03B running in place of P-9002B |  |  | 75 KW extra power consumtion for same application | [5 empty] | 9000 Rs/day |  | Attained
17 | GDP condensate transfer pump gland leak | Ground floor | GDP plant | Condensate wastage | [7 empty] | Attained
Reference for calculations of steam loss
http://www.tlv.com/global/TI/calculator/steam-flow-rate-through-orifice.html