## condensate steam calculations
| 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01
Increase in condensate recovery in MT | 160 | 440.68 | 688.91 | 438.49 | 149.92
Fuel saved in SCM | 1248.78 | 3456.31 | 5403.21 | 3439.13 | 1175.84
DM Water saving in Rs | 8757.1 | 24237.4 | 37890.5 | 24116.95 | 8245.6
Fuel saving in Rs | 28347.4 | 87444.73 | 136701 | 87010.17 | 29748.9
Condensate saving In Rs. | 37104.5 | 111682.13 | 174591.5 | 111127.12 | 37994.43
price of steam per Kg (Rs) | 1.81 | 1.9 | 1.9 | 1.9 | 1.9
Total steam save (MT) | 38.12 | 51.2 | 138.58 | 158.85 | 268.34
Steam saving in (Rs) | 68997.2 | 97280 | 263302 | 301815 | 509846
Total saving in Rs. | 106101.7 | 208962.13 | 437893.5 | 412942.12 | 547840.43
| Before shutdown |  | FOR NOVEMBER 2016 |  |  | FOR DECEMBER 2016 |  |  | Remark | FOR JAN. 2017 |  |  | Remark
Grade | Avg steam for tracing per day(MT) | Avg condensate recovery per day(m3) | Avg. steam for tracing per day (MT) | Avg. condensate recovery per day(M3) | steam saved per day | Avg. steam for tracing per day (MT) | Avg. condensate recovery per day(M3) | steam saved per day |  | Avg. steam for tracing per day (MT) | Avg. condensate recovery per day(M3)
C1214 | 35.24 | 15.8 | 29.8 | 27.247 | 5.44 | 36.43 | 28.4 | -1.19 | some steam headar valve are found passing so C1214 run not taken into the account | 42.23 | 31.7 |  | some headar valve are found passing so C1214 run not taken into the account | ,
Other grade | 43.99 | 16.02 | 42.17 | 30.89 | 1.82 | 40.79 | 31.75 | 3.2 |  | 42.84 | 40.52 | 1.15
Saving in November 2016 after shutdown
Avg condensate reacovery per day for C1214 (MT) |  | 27.247
Avg condensate reacovery per day for other grade (MT) |  | 30.89
Grade | No. of days | Total condensate recovery | Total condensate recovery | Total condensate recovery | total saving in Rs |  |  | Steam saved (MT)
|  | As per before shutdown Avg. | As per after shutdown Aug.
C1214@20Nov. | 5 | 79 | 149 | 70 | 16312.74 |  |  | 27.2
other Grade@25 Nov. | 6 | 96.12 | 185.34 | 89.22 | 20791.75 |  |  | 10.92
|  |  |  | total saving In November 2016 | 37104.49 |  |  | 38.12
Saving in December 2016
Avg condensate reacovery per day for C1214 (MT) |  | 28.4
Avg condensate reacovery per day for other grade (MT) |  | 31.75
Grade | No. of days | Total condensate recovery | Total condensate recovery | Total condensate recovery | total saving in Rs |  |  | Steam saved (MT)
|  | As per before shutdown Aug. | As per recent Avg .in Dec 2016
C1214 | 15 | 237 | 426 | 189 | 47898.52
other grad | 16 | 256.32 | 508 | 251.68 | 63783.67 |  |  | 51.2
|  |  |  | Total saving in December2016 in Rs | 111682.19 |  |  | 51.2
Savings in January 2017
Avg condensate reacovery per day for C1214 (MT) |  | 31.7
Avg condensate reacovery per day for other grade (MT) |  | 40.52
Grade | No. of days | Total condensate recovery | Total condensate recovery | Total condensate recovery | total saving in Rs | Steam saving in MT from FT702 |  |  | steam tracing for transfer line ,line up for |  |  |  | 28 | days in jan.2017 | FT702 +FT710
|  | As per before shutdown Aug. | As per recent Avg. | [5 empty] | Aug. steam taken for t/F line tracing FT710 (before attending leak ) | Avg steam taken for t/F line tracing FT710 (After attending leak ) | Total steam need for tracing as per previous Avg. |  | Total steam need for tracing as per recent Avg.in jAN. | Steam saved MT | Total steam save in MT
C1214 | 13 | 205.4 | 412.1 | 206.7 | 62828.17
other grade | 18 | 288.36 | 729.36 | 441 | 111763.23 | 20.7 |  |  | 19.43 | 15.22 | 544.04 |  | 426.16 | 117.88 | 138.58
|  |  |  | 647.7 | 174591.4 | 20.7
Savings in Feb. 2017
Avg condensate reacovery per day for C1214 (MT) |  | 39.08 | Avg steam for tracing per day for C1214 (MT) |  | 39.08
Avg condensate reacovery per day for other grade (MT) |  | 26.75 | Avg steam for tracing per day per day for other grade (MT) |  | 42.82
Grade | No. of days | Total condensate recovery | Total condensate recovery | Total condensate recovery | total saving in Rs | Steam saving in MT from FT702 |  |  | steam tracing for transfer line ,line up for |  |  | 24 | days in FEB.2017 | FT702 +FT710
|  | As per before shutdown Aug. | As per recent Avg. | [5 empty] | Avg. steam taken for t/F line tracing FT710 (before attending leak ) | Avg steam taken for t/F line tracing FT710 (After attending leak ) | Total steam need for tracing as per previous Avg. | Total steam need for tracing as per recent Avg.in FEB. | Steam saved MT | Total steam save in MT
C1214 | 11 | 173.8 | 429.88 | 256.08 | 64898
other grade | 17 | 272.34 | 454.75 | 182.41 | 46228 | 19.89 |  |  | 19.43 | 13.64 | 466.32 | 327.36 | 138.96 | 158.85
|  |  |  | 438.49 | 111126 | 19.89
Savings in March. 2017
Avg condensate reacovery per day for C1214 (MT) |  | 20.92 | Avg steam for tracing per day for C1214 (MT) |  | 32.22 |  |  |  | steam tracing for transfer line ,line up for |  |  | 22 | days in MARCH.2017 | FT702 +FT710
Avg condensate reacovery per day for other grade (MT) |  | 20.59 | Avg steam for tracing per day per day for other grade (MT) |  | 38.85 |  |  |  | Aug. steam taken for t/F line tracing FT710 (before attending leak ) | Avg steam taken for t/F line tracing FT710 (After attending leak ) | Total steam need for tracing as per previous Avg. | Total steam need for tracing as per recent Avg.in MARCH. | Steam saved MT | Total steam save in MT
Grade | No. of days | Total condensate recovery | Total condensate recovery | Total condensate recovery | total saving in Rs | Steam saving in MT from FT702 |  |  | 19.43 | 13.03 | 427.46 | 286.66 | 140.8 | 268.34
|  | As per before shutdown Aug. | As per recent Avg.
C1214 | 15 | 237 | 313.8 | 76.8 | 19463.5 | 45.3
other grade | 16 | 256.32 | 329.44 | 73.12 | 18530.9 | 82.24
|  |  |  | 149.92 | 37994.4 | 127.54
Condensate Cost calculator
condensate increases in M3 | 149.92
DM water Temp (oC ) initial | 30
Condensate Temp. oC | 90
Dm water Cost per M3 | 55
Fuel Cost per SCM | 25.3
Cp of water in Kcal/Kg oC | 1
density of water kg/m3 | 1000
efficiency of boiler | 0.9
NCV of fuel Kcal /scm | 8500
DM water saved in Rs | 8245.6
Fuel saved in scm | 1175.8431
fuel saving in Rs | 29748.8314
Total saving in Rs | 37994.4314

## totals
| FT701 | FT7111 | Total steam use | condensate return | % recovery | FT710 |  |  | FT702 | FT701 | FT7111 | Total steam use | condensate return | % recovery | FT710 | [5 empty] | FT710 before |  |  |  | FT702 | FT701 | FT7111 | Total steam use | condensate return | FT710 | [6 empty] | FT702 | FT701 | condensate return | FT710
2017-01-01 | 76.02 | 8.28 | 84.3 | 62.92 | 74.6382 | 16.4 |  | 2017-01-01 | 41.87 | 76.02 | 8.28 | 84.3 | 62.92 | 74.6382 | 16.4 |  |  |  |  | April2016 | 20.43 |  |  | 2017-02-01 | 33.078 | 0.06 | 29.06 | 29.12 | 67.526 | 0.72 |  |  | c1214 |  |  | 2017-03-01 | 43.48 | 42.144 | 34.606 | 13.91 | C1698 | 13.91
2017-01-02 | 77.296 | 1.585 | 78.881 | 30.741 | 38.9714 | 17.17 |  | 2017-01-02 | 43.046 | 77.296 | 1.585 | 78.881 | 30.741 | 38.9714 | 17.17 |  | C2280 |  |  | may | 20.51 |  |  | 2017-02-02 | 32.53 | 11.292 | 28.74 | 40.032 | 35.975 | 0.67 | [5 empty] | 2017-03-02 | 47.054 | 24.18 | 26.411 | 14.88 |  | 14.88
2017-01-03 | 77.044 | 9.561 | 86.605 | 32.968 | 38.0671 | 17.83 |  | 2017-01-03 | 43.256 | 77.044 | 9.561 | 86.605 | 32.968 | 38.0671 | 17.83 |  |  |  |  | Jun | 21.35 |  |  | 2017-02-03 | 33.056 | 0.528 | 30.51 | 31.038 | 33.584 | 0.46 | [5 empty] | 2017-03-03 | 46.392 | 23.184 | 21.778 | 14.81 |  | 14.81
2017-01-04 | 78.952 | 3.897 | 82.849 | 29.904 | 36.0946 | 18.12 |  | 2017-01-04 | 43.17 | 78.952 | 3.897 | 82.849 | 29.904 | 36.0946 | 18.12 |  |  |  |  | jully | 19.89 |  |  | 2017-02-04 | 39.07 | 8.28 | 29.78 | 38.06 | 34.031 | 3.67 | [5 empty] | 2017-03-04 | 44.04 | 3.08 | 24.003 | 14.29 |  | 14.29
2017-01-05 | 75.592 | 12.351 | 87.943 | 31.067 | 35.3263 | 17.44 |  |  | 42.8355 | 77.328 | 5.8307 | 83.1587 | 39.1333 | 46.9428 | 17.38 |  |  |  |  | Aug. | 19.89 |  |  | 2017-02-05 | 41.19 | 28.34 | 38.46 | 66.8 | 36.15 | 11.98 | [6 empty] | 45.2415 | 23.147 | 26.6995 | 14.4725
2017-01-06 | 76.196 | 9.65 | 85.846 | 30.81 | 35.8898 | 17.62 |  | 2017-01-05 | 45.684 | 75.592 | 12.351 | 87.943 | 31.067 | 35.3263 | 17.44 |  |  |  |  | September | 18.15 |  |  |  | 35.7848 | 9.7 | 31.31 | 41.01 | 41.4532 | 3.5 |  |  |  |  | 41.45 | 2017-03-05 | 38.15 | 54.668 | 16.217 | 14.18 | C1214 | 14.18
2017-01-07 | 72.92 | 30.377 | 103.297 | 29.064 | 28.1363 | 18.37 |  | 2017-01-06 | 45.618 | 76.196 | 9.65 | 85.846 | 30.81 | 35.8898 | 17.62 |  |  |  |  | October | 18.19 |  |  | 2017-02-06 | 42.22 | 50.36 | 22.35 | 72.71 | 32.58 | 12.71 |  |  | C1898 |  |  | 2017-03-06 | 29.42 | 7.95 | 19.075 | 2.15
2017-01-08 | 64.02 | 48.13 | 112.15 | 34.57 | 30.8248 | 18.56 |  | 2017-01-07 | 44.844 | 72.92 | 30.377 | 103.297 | 29.064 | 28.1363 | 18.37 |  |  |  |  | november | 17.79 |  |  | 2017-02-07 | 43.906 | 58.352 | 31.55 | 89.902 | 33.244 | 13.08 | [5 empty] | 2017-03-07 | 28.95 | 0.4 | 20.47 | 0.48
2017-01-09 | 17.17 | 76.22 | 93.39 | 32.59 | 34.8967 | 18.66 | 17.7967 | 2017-01-08 | 48.57 | 64.02 | 48.13 | 112.15 | 34.57 | 30.8248 | 18.56 |  | C1214 |  |  | Dec | 19.04 |  |  | 2017-02-08 | 43.478 | 49.252 | 45.7 | 94.952 | 26.524 | 13.39 | [5 empty] | 2017-03-08 | 31.574 | 0 | 20.87 | 0.58
2017-01-10 | 0.004 | 86.33 | 86.334 | 28.48 | 32.9882 | 3.47 |  | 2017-01-09 | 42.67 | 17.17 | 76.22 | 93.39 | 32.59 | 34.8967 | 18.66 | [5 empty] | 19.4711 |  |  | 2017-02-09 | 42.218 | 46.144 | 14.52 | 60.664 | 27.888 | 13 | [5 empty] | 2017-03-09 | 30.268 | 7.024 | 21.912 | 6.6
2017-01-11 | 0 | 82.91 | 82.91 | 31.291 | 37.7409 | 0.75 |  | 2017-01-10 | 39.76 | 0.004 | 86.33 | 86.334 | 28.48 | 32.9882 | 3.47 | [9 empty] | 42.9555 | 51.027 | 28.53 | 79.557 | 30.059 | 13.045 |  |  |  | 30.06 |  | 2017-03-10 | 29.35 | 1.192 | 24.376 | 13.25 |  | 13.25
2017-01-12 | 0.008 | 95.349 | 95.357 | 34.02 | 35.6765 | 9.45 |  | 2017-01-11 | 38.498 | 0 | 82.91 | 82.91 | 31.291 | 37.7409 | 0.75 |  |  |  |  | jan2017 | 15.22 |  |  | 2017-02-10 | 42.396 | 45.132 | 26.03 | 71.162 | 22.179 | 12.63 | [5 empty] | 2017-03-11 | 30.684 | 0 | 24.338 | 14.15 |  | 14.15
2017-01-13 | 50.908 | 37.049 | 87.957 | 37.901 | 43.0904 | 13.14 |  | 2017-01-12 | 40.398 | 0.008 | 95.349 | 95.357 | 34.02 | 35.6765 | 9.45 | [8 empty] | 2017-02-11 | 43.714 | 64.956 | 27.95 | 92.906 | 28.287 | 13.62 | [5 empty] | 2017-03-12 | 33.39 | 23.416 | 22.448 | 13.34 |  | 13.34
2017-01-14 | 5.13 | 86.63 | 91.76 | 43.25 | 47.1338 | 14.51 |  |  | 43.2552 | 38.2388 | 55.1646 | 93.4034 | 31.5464 | 33.9349 | 13.04 | [8 empty] | 2017-02-12 | 41.202 | 61.58 | 26.73 | 88.31 | 25.42 | 12.97 | [5 empty] | 2017-03-13 | 43.3 | 55.004 | 22.075 | 12.75 |  | 12.75
2017-01-15 | 1.124 | 85.311 | 86.435 | 51.288 | 59.3371 | 15.33 |  | 2017-01-13 | 41.602 | 50.908 | 37.049 | 87.957 | 37.901 | 43.0904 | 13.14 | [5 empty] | 42.8355 |  |  | 2017-02-13 | 44.3 | 49.996 | 28.36 | 78.356 | 27.62 | 13.51 |  |  | C1618TA |  |  |  | 32.7873 | 16.6282 | 21.309 | 8.6089 |  | 13.534
2017-01-16 | 14.04 | 75.73 | 89.77 | 39.67 | 44.1907 | 14.38 |  | 2017-01-14 | 49.94 | 5.13 | 86.63 | 91.76 | 43.25 | 47.1338 | 14.51 | [6 empty] | 43.2552 |  | 2017-02-14 | 42.956 | 56.98 | 30.3 | 87.28 | 25.622 | 13.25 | [5 empty] | 2017-03-14 | 43.09 | 49.272 | 38.27 | 12.2 | C1618TA | 12.2
2017-01-17 | 18.432 | 74.34 | 92.772 | 52.851 | 56.9687 | 14.25 |  | 2017-01-15 | 47.79 | 1.124 | 85.311 | 86.435 | 51.288 | 59.3371 | 15.33 | [5 empty] | 44.6846 |  |  | 2017-02-15 | 42.154 | 51.052 | 28.93 | 79.982 | 26.761 | 13.25 | [5 empty] | 2017-03-15 | 42.312 | 47.332 | 21.114 | 12.52 |  | 12.52
2017-01-18 | 10.46 | 75.992 | 86.452 | 51.955 | 60.0969 | 13.61 |  | 2017-01-16 | 47.03 | 14.04 | 75.73 | 89.77 | 39.67 | 44.1907 | 14.38 |  | C1618TA |  |  |  |  | 42.27 |  | 2017-02-16 | 42.654 | 50.808 | 28.42 | 79.228 | 24.124 | 14.01 | [5 empty] | 2017-03-16 | 36.294 | 35.684 | 18.486 | 10.56 |  | 10.56
|  | Avg | 89.7227 | 38.0744 | 42.7816 | 13.5243 |  | 2017-01-17 | 47.774 | 18.432 | 74.34 | 92.772 | 52.851 | 56.9687 | 14.25 | [5 empty] | 41.2023 |  |  |  | 42.768 | 54.3577 | 28.1029 | 82.4606 | 25.7161 | 13.32 |  |  |  | 25.72 |  | 2017-03-17 | 39.6 | 44.8 | 20.78 | 12.16 |  | 12.16
| FT701 | FT7111 | Total steam use | condensate return | % recovery | FT710 |  | 2017-01-18 | 46.68 | 10.46 | 75.992 | 86.452 | 51.955 | 60.0969 | 13.61 | [5 empty] | 42.9075 | 42.7626 |  | 2017-02-17 | 44.548 | 56.56 | 26.81 | 83.37 | 27.267 | 13.66 | [5 empty] | 2017-03-18 | 41.146 | 49.38 | 23.55 | 12.09 |  | 12.09
2016-12-01 | 74.98 | 1.986 | 76.966 | 64.44 | 83.7253 | 17.82 |  | 2017-01-19 | 41.254 | 37.448 | 42.992 | 80.44 | 46.375 | 57.6517 | 13.3 | [8 empty] | 2017-02-18 | 43.096 | 64.656 | 26.08 | 90.736 | 23.734 | 13.59 | [5 empty] | 2017-03-19 | 41.412 | 39.584 | 23.131 | 12.18 |  | 12.18
2016-12-02 | 42.2778 | 41.015 | 83.2928 | 19.67 | 23.6155 | 17.52 |  | 2017-01-20 | 40.244 | 40.44 | 39.593 | 80.033 | 43.96 | 54.9273 | 12.6 |  |  |  |  | 42.84 | 39.13 |  |  | 2017-02-19 | 42.234 | 54.312 | 26.84 | 81.152 | 26.62 | 13.28 |  |  | C1618FA |  |  |  | 40.6423 | 44.342 | 24.2218 | 11.9517
2016-12-03 | 22.596 | 60.256 | 82.852 | 22.356 | 26.9831 | 19.78 |  | 2017-01-21 | 42.56 | 47.572 | 36.144 | 83.716 | 41.155 | 49.1603 | 12.85 |  |  |  | 43.26 |  |  | 31.49 |  | 2017-02-20 | 41.26 | 70.088 | 24.02 | 94.108 | 26.211 | 13.76 | [5 empty] | 2017-03-20 | 41.16 | 33.5 | 21.123 | 13.14 | C1618FA | 13.14
2016-12-04 | 4.48 | 64.077 | 68.557 | 26.047 | 37.9932 | 18.78 |  | 2017-01-22 | 41.972 | 52.196 | 38.215 | 90.411 | 43.665 | 48.2961 | 13.93 |  |  |  |  | 44.68 | 45.21 |  |  |  | 42.7845 | 61.404 | 25.9375 | 87.3415 | 25.958 | 13.5725 |  |  |  | 25.96 |  | 2017-03-21 | 39.36 | 17.088 | 21.82 | 11.45 |  | 11.45
2016-12-05 | 6.3 | 31 | 37.3 | 29.5 | 79.0885 | 19.4 |  |  | 44.6846 | 27.775 | 59.1996 | 86.9746 | 45.207 | 52.0853 | 13.79 |  |  |  |  | 42.26 | 37.22 |  |  | 2017-02-21 | 39.96 | 25.81 | 23.32 | 49.13 | 26.19 | 14.33 |  |  | C1214 |  |  | 2017-03-22 | 40.67 | 33.264 | 21.118 | 11.75 |  | 11.75
2016-12-06 | 38.84 | 1.01 | 39.85 | 30.51 | 76.5621 | 18.15 |  | 2017-01-23 | 42.166 | 50.952 | 47.11 | 98.062 | 39.852 | 40.6396 | 14.44 |  |  |  | 41.2 |  |  | 31.92 |  | 2017-02-22 | 42.184 | 27.58 | 59.58 | 87.16 | 26.126 | 14.46 | [6 empty] | 40.3967 | 27.9507 | 21.3537 | 12.1133
2016-12-07 | 44.136 | 49.33 | 93.466 | 31.266 | 33.4517 | 19.4 |  | 2017-01-24 | 41.86 | 49.48 | 44.144 | 93.624 | 36.96 | 39.4771 | 14.24 |  |  |  | 42.23 | 43.26 | 40.52 | 31.705 |  | 2017-02-23 | 41.784 | 18.36 | 28.89 | 47.25 | 28.05 | 14.21 | [5 empty] | 2017-03-23 | 41.56 | 56.172 | 21.118 | 4.53 | C1214
2016-12-08 | 49.46 | 40.31 | 89.77 | 35.5 | 39.5455 | 18.04 |  | 2017-01-25 | 42.784 | 43.18 | 54.965 | 98.145 | 34.86 | 35.5189 | 14.96 |  | C1618FA | [6 empty] | 2017-02-24 | 44.048 | 11.5 | 30.17 | 41.67 | 25.585 | 14.76 | [5 empty] | 2017-03-24 | 31.284 | 8.224 | 19.402 | 1.28
2016-12-09 | 48.78 | 40.52 | 89.3 | 29.061 | 32.5431 | 18.98 |  |  | 42.27 | 47.8707 | 48.7397 | 96.6103 | 37.224 | 38.5452 | 14.5467 | [8 empty] | 2017-02-25 | 46.848 | 0.416 | 30.88 | 31.296 | 28.494 | 15.16 | [5 empty] | 2017-03-25 | 31.63 | 16.928 | 23.108 | 1.07
2016-12-10 | 68.47 | 23.069 | 91.539 | 33.87 | 37.0006 | 19.9 |  | 2017-01-26 | 44.29 | 48.3 | 48.32 | 96.62 | 37.4 | 38.7083 | 14.9 | [8 empty] | 2017-02-26 | 39.466 | 21.156 | 32.1 | 53.256 | 20.862 | 13.46 | [5 empty] | 2017-03-26 | 29.528 | 14.916 | 19.082 | 0.93
2016-12-11 | 25.53 | 52.22 | 77.75 | 27.35 | 35.1768 | 19.29 |  | 2017-01-27 | 42.08 | 67.172 | 22.627 | 89.799 | 32.844 | 36.575 | 14.62 | [9 empty] | 42.3817 | 17.4703 | 34.1567 | 51.627 | 25.8845 | 14.3967 |  |  |  |  | 25.88 | 2017-03-27 | 30.782 | 0 | 20.34 | 5.86
2016-12-12 | 17.192 | 55.934 | 73.126 | 27.247 | 37.2603 | 20.65 |  | 2017-01-28 | 41.61 | 35.32 | 49.66 | 84.98 | 30.38 | 35.7496 | 13.64 | [8 empty] | 2017-02-27 | 43.09 | 32.12 | 31.97 | 64.09 | 24.96 | 13.39 |  |  | C1698 |  |  | 2017-03-28 | 25.096 | 0 | 20.099 | 13.9 |  | 13.9
2016-12-13 | 24.7 | 61.52 | 86.22 | 25.027 | 29.0269 | 20.21 |  | 2017-01-29 | 41.43 | 0.788 | 86 | 86.788 | 32.78 | 37.7702 | 2.14 | [8 empty] | 2017-02-28 | 46.66 | 5.76 | 31.64 | 37.4 | 25.67 | 14.36 | [6 empty] | 31.6467 | 16.04 | 20.5248 | 4.595
2016-12-14 | 15.86 | 54.35 | 70.21 | 25.57 | 36.4193 | 19.53 |  | 2017-01-30 | 39.952 | 0 | 86.071 | 86.071 | 29.648 | 34.446 | 0.72 |  | C1214 | [7 empty] | 44.875 | 18.94 | 31.805 | 50.745 | 25.315 | 13.875 |  |  |  | 25.32 |  | 2017-03-29 | 31.378 | 37.612 | 21.719 | 12.67 | C1898 | 12.67
2016-12-15 | 26.34 | 56.86 | 83.2 | 26.766 | 32.1707 | 19.97 |  | 2017-01-31 | 37.852 | 0.02 | 86.562 | 86.582 | 28.463 | 32.874 | 0.58 | [14 empty] | 13.6446 | [5 empty] | 2017-03-30 | 39.344 | 32.996 | 20.598 | 12.93 |  | 12.93
2016-12-16 | 2.408 | 76.54 | 78.948 | 24.69 | 31.2737 | 18.62 |  |  | 41.2023 | 25.2667 | 63.2067 | 88.4733 | 31.9192 | 36.0205 | 7.7667 | [20 empty] | 2017-03-31 | 16.692 | 17.664 | 8.968 | 3.79
2016-12-17 | 14.2 | 67.63 | 81.83 | 24.24 | 29.6224 | 19.26 | [30 empty] | 29.138
2016-12-18 | 40.23 | 45.47 | 85.7 | 22.41 | 26.1494 | 19.06 | [20 empty] | 35.78
2016-12-19 | 32.81 | 54.29 | 87.1 | 25.67 | 29.4719 | 19.65 | [20 empty] | 42.38
2016-12-20 | 25.44 | 59.073 | 84.513 | 26.58 | 31.4508 | 19.5
2016-12-21 | 22.94 | 60 | 82.94 | 28.7 | 34.6033 | 20.02
2016-12-22 | 41.48 | 42.43 | 83.91 | 25.23 | 30.0679 | 18.49
2016-12-23 | 52.79 | 33.44 | 86.23 | 31.857 | 36.9442 | 17.9
2016-12-24 | 53.2 | 42.202 | 95.402 | 32.976 | 34.5653 | 19.24
2016-12-25 | 62.31 | 32.78 | 95.09 | 32.99 | 34.6934 | 19.52
2016-12-26 | 44.14 | 38.79 | 82.93 | 30.28 | 36.5127 | 18.08
2016-12-27 | 10.476 | 67.926 | 78.402 | 33.977 | 43.3369 | 18.15
2016-12-28 | 0 | 85.23 | 85.23 | 34.17 | 40.0915 | 18.44
2016-12-29 | 7.608 | 66.78 | 74.388 | 31.411 | 42.2259 | 18.32
2016-12-30 | 1.652 | 83.687 | 85.339 | 35.983 | 42.1648 | 19.4
2016-12-31 | 17 | 69 | 86 | 36 | 41.8605 | 19.11
|  | Avg. | 80.5597 | 30.0434 | 38.8902 | 19.0381
2016-11-01 | 71.732 | 22.29 | 94.022 | 15.28 | 16.2515 | 16.72
2016-11-02 | 74 | 25.6 | 99.6 | 13.1 | 13.1526 | 18
2016-11-03 | 70.8 | 20 | 90.8 | 16.8 | 18.5022 | 17.1
2016-11-04 | 59.7 | 28.8 | 88.5 | 19 | 21.4689 | 18
2016-11-05 | 56.2 | 32 | 88.2 | 13.5 | 15.3061 | 17.5
2016-11-06 | 69.76 | 19.37 | 89.13 | 16.87 | 18.9274 | 17.37
2016-11-07 | 73.69 | 1.724 | 75.414 | 13.33 | 17.6758 | 17.16
2016-11-08 | 53.26 | 14.19 | 67.45 | 16.11 | 23.8844 | 4.69
2016-11-09 | 39.832 | 13.956 | 53.788 | 20.402 | 37.9304 | 0.4
2016-11-10 | 38.864 | 13.83 | 52.694 | 19.041 | 36.135 | 0.33
2016-11-11 | 38.85 | 13.93 | 52.78 | 17.77 | 33.6681 | 0.33
2016-11-12 | 51.4 | 12.35 | 63.75 | 21.22 | 33.2863 | 0.29
2016-11-13 | 60.472 | 6.978 | 67.45 | 17.81 | 26.4047 | 2.49
2016-11-14 | 86.52 | 0 | 86.52 | 20.978 | 24.2464 | 1.38
2016-11-15 | 22.56 | 0 | 22.56 | 5.28 | 23.4043 | 0.58 |  | 16.941 | 75.6598 | 24.0456
2016-11-16 | 8.87 | 1.027 | 9.897 | 2.075 | 20.9659 | 0.43 |  | 24.2779 | 84.6428 | 29.1636
2016-11-17 | 24.3 | 16.4 | 40.7 | 7.2 | 17.6904 | 0.56 |  | 20.6095 | 80.1513 | 26.6046
2016-11-18 | 33.85 | 24.51 | 58.36 | 17.54 | 30.0548 | 0.4
2016-11-19 | 42.45 | 32.166 | 74.616 | 19.19 | 25.7183 | 0.3
2016-11-20 | 48.78 | 25.21 | 73.99 | 22.84 | 30.869 | 0.38
2016-11-21 | 68 | 13.9 | 81.9 | 21.08 | 25.7387 | 2.51
2016-11-22 | 33.6 | 53.1 | 86.7 | 29.5 | 34.0254 | 17.4
2016-11-23 | 34.876 | 49.154 | 84.03 | 24.627 | 29.3074 | 16.37
2016-11-24 | 15.1 | 67.4 | 82.5 | 26.3 | 31.8788 | 19.1
2016-11-25 | 50.808 | 32.601 | 83.409 | 27.301 | 32.7315 | 18.87
2016-11-26 | 60.54 | 38.277 | 98.817 | 23.039 | 23.3148 | 19.17
2016-11-27 | 67.676 | 27.506 | 95.182 | 25.577 | 26.8717 | 17.85
2016-11-28 | 66.428 | 40.642 | 107.07 | 21.753 | 20.3166 | 19.43
2016-11-29 | 37.224 | 34.573 | 71.797 | 21.83 | 30.4052 | 16.38
2016-11-30 | 47.016 | 18.66 | 65.676 | 23.21 | 35.3402 | 18.29
|  | Avg. | 73.5767 | 18.6518 | 25.8491 | 9.9927
2016-10-01 | 48.3 | 19.49 | 67.79 | 16.27 | 24.0006 | 15.37
2016-10-02 | 41.9 | 28.28 | 70.18 | 14.72 | 20.9746 | 19.97
2016-10-03 | 17.804 | 37.452 | 55.256 | 15.219 | 27.5427 | 18.24
2016-10-04 | 35.672 | 31.69 | 67.362 | 15.87 | 23.5593 | 19.41
2016-10-05 | 46.88 | 26.89 | 73.77 | 16.11 | 21.8381 | 19.28
2016-10-06 | 45.139 | 41.468 | 86.607 | 18.081 | 20.8771 | 20.31
2016-10-07 | 72.84 | 23.94 | 96.78 | 17.99 | 18.5886 | 18.59
2016-10-08 | 79.44 | 18.74 | 98.18 | 16.11 | 16.4086 | 18.2
2016-10-09 | 68.06 | 24.77 | 92.83 | 20.004 | 21.5491 | 18.51 | [8 empty] | 19.7
2016-10-10 | 80.26 | 15.74 | 96 | 9.57 | 9.9688 | 18.48
2016-10-11 | 75.656 | 20.022 | 95.678 | 15.923 | 16.6423 | 17.88
2016-10-12 | 74.608 | 25.407 | 100.015 | 14.407 | 14.4048 | 18.19
2016-10-13 | 62.232 | 35.6 | 97.832 | 16.688 | 17.0578 | 19.43
2016-10-14 | 59.772 | 39.04 | 98.812 | 20.017 | 20.2577 | 19.3
2016-10-15 | 75.224 | 14.039 | 89.263 | 18.49 | 20.7141 | 18.08
2016-10-16 | 37.74 | 54.028 | 91.768 | 15.737 | 17.1487 | 17.89
2016-10-17 | 20.3 | 72.62 | 92.92 | 20.98 | 22.5786 | 18.31
2016-10-18 | 30.88 | 66.709 | 97.589 | 13.84 | 14.1819 | 18.41
2016-10-19 | 30.88 | 60.25 | 91.13 | 17.76 | 19.4886 | 18.04
2016-10-20 | 45.932 | 56.371 | 102.303 | 17.854 | 17.4521 | 18.97
2016-10-21 | 51.496 | 44.424 | 95.92 | 18.091 | 18.8605 | 18
2016-10-22 | 62.3 | 35.3 | 97.6 | 16.94 | 17.3566 | 20.3
2016-10-23 | 74.48 | 19.96 | 94.44 | 21.57 | 22.8399 | 18.5
2016-10-24 | 69.888 | 33.026 | 102.914 | 15.277 | 14.8444 | 19.68
2016-10-25 | 73.21 | 27.16 | 100.37 | 18.26 | 18.1927 | 19.03
2016-10-26 | 68.16 | 28.61 | 96.77 | 18.52 | 19.1382 | 18.32
2016-10-27 | 69.71 | 27.04 | 96.75 | 21.1 | 21.8088 | 18.36
2016-10-28 | 69.6 | 26.79 | 96.39 | 20.45 | 21.2159 | 18.39
2016-10-29 | 53.68 | 41.97 | 95.65 | 18.88 | 19.7386 | 19.23
2016-10-30 | 65.016 | 27.36 | 92.376 | 10.86 | 11.7563 | 17.6
2016-10-31 | 60.124 | 35.549 | 95.673 | 15.463 | 16.1623 | 18.2
|  | Avg | 91.1909 | 17.0016 | 18.9403 | 18.5958
2016-09-01 | 87.836 | 11.495 | 99.331 | 7.428 | 7.478 | 11.31
2016-09-02 | 32.8 | 56.4 | 89.2 | 13.8 | 15.4709 | 8.4
2016-09-03 | 17.4 | 62.2 | 79.6 | 11.31 | 14.2085 | 20.2
2016-09-04 | 28.91 | 54.83 | 83.74 | 12.43 | 14.8436 | 21.06
2016-09-05 | 27 | 60.66 | 87.66 | 18.45 | 21.0472 | 22.19
2016-09-06 | 17.66 | 57.83 | 75.49 | 18.31 | 24.2549 | 4.94
2016-09-07 | 20.568 | 52.535 | 73.103 | 17.094 | 23.3834 | 19.28
2016-09-08 | 65.2 | 50.9 | 116.1 | 19.7 | 16.9681 | 20.4 |  | 13.8 | 7.428 | 11.31 | 12.43 | 18.45 | 18.31 | 17.094 |  | 22.9 | 13.33 | 16.04 | 17.215 | 12.39 | 9.23 | 19.75 | 18.4 | 15.99 | 14.93 | 7.756 | 9.8 | 13.1 | 12.8 | 14.2 | 10.84 | 15.89 | 11.17 | 8.993 | 11.192 | 12.78
2016-09-09 | 40.85 | 52.56 | 93.41 | 22.9 | 24.5156 | 20.3
2016-09-10 | 55.88 | 34.62 | 90.5 | 13.33 | 14.7293 | 19.07
2016-09-11 | 62.99 | 34.5 | 97.49 | 16.04 | 16.453 | 19.43
2016-09-12 | 74.34 | 33.527 | 107.867 | 17.215 | 15.9595 | 20.45
2016-09-13 | 72.68 | 12.86 | 85.54 | 12.39 | 14.4845 | 19.17
2016-09-14 | 64.34 | 28.15 | 92.49 | 9.23 | 9.9795 | 20.33
2016-09-15 | 47.52 | 52.42 | 99.94 | 19.75 | 19.7619 | 21.9
2016-09-16 | 34.46 | 48.89 | 83.35 | 18.4 | 22.0756 | 21.19
2016-09-17 | 24.66 | 55.52 | 80.18 | 15.99 | 19.9426 | 20.66
2016-09-18 | 15.83 | 49.23 | 65.06 | 14.93 | 22.948 | 20.28
2016-09-19 | 17.692 | 33.162 | 50.854 | 7.756 | 15.2515 | 18.95
2016-09-20 | 32 | 31.3 | 63.3 | 9.8 | 15.4818 | 13.08
2016-09-21 | 36.6 | 42.1 | 78.7 | 13.1 | 16.6455 | 27
2016-09-22 | 68.9 | 32.4 | 101.3 | 12.8 | 12.6357 | 21.7
2016-09-23 | 78.7 | 28.8 | 107.5 | 17.4 | 16.186 | 19.4
2016-09-24 | 84.3 | 10 | 94.3 | 14.2 | 15.0583 | 20.1
2016-09-25 | 83.9 | 5.07 | 88.97 | 10.84 | 12.1839 | 19.95
2016-09-26 | 79.7 | 13.27 | 92.97 | 15.89 | 17.0915 | 18.3
2016-09-27 | 79.27 | 17.74 | 97.01 | 11.17 | 11.5143 | 18.46
2016-09-28 | 51.892 | 25.691 | 77.583 | 8.993 | 11.5915 | 16.41
2016-09-29 | 51.052 | 26.572 | 77.624 | 11.192 | 14.4182 | 17.38
2016-09-30 | 49.67 | 10.791 | 60.461 | 12.78 | 21.1376 | 3.34
|  | Avg. | 86.3541 | 14.1539 | 16.59 | 18.1543
2016-08-01 | 15.744 | 84.56 | 100.304 | 19.1 | 19.0421 | 7.93
2016-08-02 | 33.42 | 52.61 | 86.03 | 14.15 | 16.4478 | 21.97
2016-08-03 | 92.4 | 12.26 | 104.66 | 18.91 | 18.068 | 22.55
2016-08-04 | 95.43 | 0.095 | 95.525 | 14.98 | 15.6818 | 19.84
2016-08-05 | 96.5 | 0.3 | 96.8 | 10.74 | 11.095 | 19.4
2016-08-06 | 96.84 | 0.16 | 97 | 10.16 | 10.4742 | 20.06
2016-08-07 | 97 | 2.5 | 99.5 | 11.3 | 11.3568 | 20.1
2016-08-08 | 97.936 | 0.065 | 98.001 | 10.086 | 10.2917 | 20.25
2016-08-09 | 44.43 | 4.749 | 49.179 | 8.7 | 17.6905 | 22
2016-08-10 | 101.8 | 15.6 | 117.4 | 14.6 | 12.4361 | 23.53
2016-08-11 | 67.59 | 58.304 | 125.894 | 13.32 | 10.5803 | 24.86
2016-08-12 | 65.726 | 49.117 | 114.843 | 12.272 | 10.6859 | 21.99
2016-08-13 | 58.168 | 64.291 | 122.459 | 11.087 | 9.0536 | 23.98
2016-08-14 | 20.402 | 104.307 | 124.709 | 11.598 | 9.3001 | 15.28
2016-08-15 | 1.484 | 110.11 | 111.594 | 15.61 | 13.9882 | 6.94
2016-08-16 | 45.306 | 66.522 | 111.828 | 21.25 | 19.0024 | 22.65
2016-08-17 | 88.888 | 17.172 | 106.06 | 18.109 | 17.0743 | 20.98
2016-08-18 | 87.48 | 18.857 | 106.337 | 13.122 | 12.34 | 21.49
2016-08-19 | 87.67 | 15.63 | 103.3 | 12.78 | 12.3717 | 19.94
2016-08-20 | 89.45 | 17.83 | 107.28 | 12.96 | 12.0805 | 20.71
2016-08-21 | 85.23 | 19.05 | 104.28 | 14.35 | 13.761 | 21.43
2016-08-22 | 91.7 | 2.023 | 93.723 | 10.57 | 11.2779 | 19.38
2016-08-23 | 92.09 | 0.005 | 92.095 | 7.761 | 8.4272 | 19.6
2016-08-24 | 83.9 | 20.69 | 104.59 | 9.039 | 8.6423 | 17.77
2016-08-25 | 106.3 | 21.432 | 127.732 | 14.451 | 11.3135 | 20.56
2016-08-26 | 57.7 | 10.864 | 68.564 | 13.651 | 19.9099 | 20.61
2016-08-27 | 65.816 | 11.518 | 77.334 | 17.835 | 23.0623 | 22.19
2016-08-28 | 66.356 | 35.207 | 101.563 | 10.388 | 10.2281 | 18.57
2016-08-29 | 78.008 | 27.43 | 105.438 | 11.222 | 10.6432 | 19.9
2016-08-30 | 79.376 | 25.581 | 104.957 | 15.039 | 14.3287 | 19.47
2016-08-31 | 81.9 | 26.1 | 108 | 20.4 | 18.8889 | 20.62
|  | Avg. | 102.1606 | 13.5335 | 13.5337
2016-07-01 | 59.7 | 36 | 95.7 | 14.5 | 15.1515 | 17.5
2016-07-02 | 64.24 | 43.22 | 107.46 | 20.38 | 18.9652 | 20.32
2016-07-03 | 91.68 | 15.37 | 107.05 | 15.63 | 14.6007 | 19.5
2016-07-04 | 66.44 | 38.05 | 104.49 | 17.9 | 17.1308 | 20.16
2016-07-05 | 19.88 | 55.49 | 75.37 | 13.46 | 17.8586 | 18.76
2016-07-06 | 8.97 | 61.1 | 70.07 | 13.24 | 18.8954 | 20.222
2016-07-07 | 10.44 | 56.13 | 66.57 | 13.91 | 20.8953 | 20.52
2016-07-08 | 12.43 | 57.98 | 70.41 | 11.26 | 15.992 | 21.22
2016-07-09 | 29.6 | 54.4 | 84 | 18 | 21.4286 | 9.85
2016-07-10 | 42.95 | 67.78 | 110.73 | 23.28 | 21.0241 | 24.58
2016-07-11 | 65.72 | 21.33 | 87.05 | 34.42 | 39.5405 | 25.5
2016-07-12 | 81.1 | 30.71 | 111.81 | 19.96 | 17.8517 | 23.62
2016-07-13 | 79.08 | 39.16 | 118.24 | 21.34 | 18.048 | 21.66
2016-07-14 | 64.23 | 49.72 | 113.95 | 15.89 | 13.9447 | 22.55
2016-07-15 | 65.59 | 51.53 | 117.12 | 20.61 | 17.5973 | 22.08
2016-07-16 | 65.95 | 31.33 | 97.28 | 11.97 | 12.3047 | 20.6
2016-07-17 | 64.88 | 29.23 | 94.11 | 14.108 | 14.991 | 21.42
2016-07-18 | 63.7 | 32.7 | 96.4 | 13.1 | 13.5892 | 22.68
2016-07-19 | 79.64 | 31.05 | 110.69 | 13.2 | 11.9252 | 22.11
2016-07-20 | 82.5 | 30.54 | 113.04 | 13.2 | 11.6773 | 5.5
2016-07-21 | 83.2 | 25.6 | 108.8 | 11.9 | 10.9375 | 1.43
2016-07-22 | 79.5 | 38.3 | 117.8 | 12.7 | 10.781 | 10.05
2016-07-23 | 83.34 | 28.23 | 111.57 | 15.98 | 14.3228 | 23.89
2016-07-24 | 91 | 8.116 | 99.116 | 12.73 | 12.8435 | 21.01
2016-07-25 | 50.59 | 47.42 | 98.01 | 13.34 | 13.6109 | 23.6
2016-07-26 | 19.17 | 43.58 | 62.75 | 13.15 | 20.9562 | 23
2016-07-27 | 15.64 | 69.5 | 85.14 | 13.15 | 15.4451 | 22.36
2016-07-28 | 13.84 | 63.69 | 77.53 | 14.07 | 18.1478 | 22
2016-07-29 | 10.91 | 68.241 | 79.151 | 16.9 | 21.3516 | 21.98
2016-07-30 | 10.84 | 64.58 | 75.42 | 14.34 | 19.0135 | 22.4
2016-07-31 | 15.98 | 71.736 | 87.716 | 14.702 | 16.7609 | 20.62
|  | Avg. | 95.3078 | 15.8813 | 17.0188 | 19.7643
2016-05-01
28.82
22.69
23.45
23.48
24.99
23.6
23.53
23.36
23.72
22.95
21.92
20.15
20.5
7.11
3.77
9.05
14.63
14.67
18.42
20.76
19.78
15.93
16.65
17.28
17.98
19.9
20.01
20.23
19.65
20
[6 empty] | 17.6 | 20.5946
jun
17.5
20.32
19.5
20.16
18.76
20.222
20.52
21.22
9.85
24.58
25.5
23.62
21.66
22.55
22.08
20.6
21.42
22.68
22.11
5.5
1.43
10.05
23.89
21.01
23.6
23
22.36
22
21.98
22.4
21.3071
april
26.44
22.4
8.5
5.59
5.45
13.66
22.25
25.14
25
23.07
23.25
24.15
22.4
22.7
25.71
25.2
22.5
20.02
20.68
21.2
20.2
19.24
19.43
20.46
20.35
20.02
21.35
22.33
21.7
22.54
20.431

## job done,
steam related job | handover date | job complited date
steam leak from LP steam heder at 1st floor near 03D2 | 16.11.2016 | 15.11.2016
steam line leak on 1st floor ( resude vacuum equalization line ) | 16.11.2016 | 17.11.2016
proper steam tracing should be provided at bottom line of 01E12 to reciver | 16.11.2016 | 16.11.2016
Horizontal booster of new vacuum system (03D2) leak from jacket(welding) | 16.11.2016 | 17.11.2016
tracing line leak of 01D4 circulation line | 15.11.2016 | 15.11.2016
leak inside insulation of 01D11 bottom line | 16.11.2016 | 16.11.2016
Section 2 circulation line , o/l shoud be given on tracing line | 19.11.2016 | 19.11.2016
section4 feed line -steam trasing line leak near slope tank | 16.11.2016 | 17.11.2016
Job done related to condensate recovery in Nov 2016. shutdown
1. Condensate recovery is done for horizontal boosters of new vacuum system
2. Steam tracing line for discharge line of pump 01G15A ,connected to nearest condensate header
3. Flange leak of condensate return line near condensate recovery tank of alcohol plant attended
4. Gasket leak of condensate return line at end flange near pastillator attended
5. Steam tracing line for pump 01G4A discharge line connected to nearest condensate return line
6. Flange leak near slope tank attended
1. maintanance of condesate header (FAP to tankfarm transfer line ) opposite to linde reformer |  | 5 valve | 2

## steam consumption reduction
Job done related to condensate recovery in Nov 2016. shutdown
[6 empty] | 2015-16 |  |  |  |  | 2016-17
1. Condensate recovery is done for horizontal boosters of new vacuum system | [5 empty] | MT | MT |  |  |  | MT | MT
2. Steam tracing line for discharge line of pump 01G15A ,connected to nearest condensate header |  |  |  |  | Month | FT 701 | FT704 |  |  | Month | FT 701 | FT704
3. Flange leak of condensate return line near condensate recovery tank of alcohol plant attended |  |  |  |  | April | 1260 | 766 |  |  | April | 2011 | 594
4. Gasket leak of condensate return line at end flange near pastillator attended |  |  |  |  | May | 2053 | 954 |  |  | May | 1969 | 494
5. Steam tracing line for pump 01G4A discharge line connected to nearest condensate return line |  |  |  |  | June | 2240 | 880 |  |  | June | 1591 | 734.8
6. Flange leak near slope tank attended |  |  |  |  | July | 2136 | 1071 |  |  | July | 1592 | 654.76
[5 empty] | August | 2407 | 900 |  |  | August | 2190 | 740.8
[5 empty] | September | 1645 | 914 |  |  | September | 1504 | 689
[5 empty] | October | 1914 | 696 |  |  | October | 1767 | 712
[5 empty] | November | 2162 | 752 |  |  | November | 1507 | 585
| Before shutdown |  | After shutdown |  | December | 1401 | 661 |  |  | December | 912 | 581
Grade | Avg steam for tracing per day | Avg condensate recovery per day | Avg steam for tracing per day | Avg condensate recovery per day | January | 1062.25 | 551.56 |  |  | January | 1188 | 619
C1214 | 35.24 | 15.8 | 29.8 | 27.247 | February | 799.1 | 599.76 |  |  | February | 1021 | 545
Other grade | 43.99 | 16.02 | 42.17 | 30.89 | March | 1366 | 644.85 |  |  | March | 726 | 514
[5 empty] | Total | 20445.35 | 9390.17 |  |  | Total | 17978 | 7463.36
[5 empty] | Total steam | 29835.52 |  |  |  | Total steam | 25441.36
Avg. steam for tracing line and condensate recovery data from April 2016
2016-04-01
Grade | from | To | FT702 | condensate recover |  |  |  | %tage reduction in steam usage | 14.7279
V1214 | 2016-04-11 | 17/4/2016 | 25.273 | 18.16
V1214 | 2016-05-01 | 2016-05-10 | 32.21 | 19.062
V1214 | 19/5/2016 | 23/5/2016 | 30.8375 | 12.255
V1214 | 19/6/2016 | 22/6/2016 | 40.49 | 17.73
V1214 | 2016-04-07 | 2016-10-07 | 33.0783 | 14.6283
V1214 | 24/7/2016 | 2016-08-02 | 32.734 | 14.5632
V1214 | 2016-08-09 | 16/8/2016 | 49.872 | 13.5546
V1214 | 2016-09-01 | 2016-09-08 | 35.8623 | 14.8153
V1214 | 13/9/2016 | 22/9/2016 | 27.62 | 13.41
V1214 | 29/9/2016 | 2016-10-06 | 27.742 | 15.03
V1214 | 2016-10-10 | 15/10/2016 | 42.73 | 15.84
V1214 | 23/10/2016 | 30/10/2016 | 43.37 | 18.1146
V1214 | 2016-11-07 | 14/11/2016 | 36.42 | 18.33
|  | Avg. | 35.2492 | 15.8072
After shutdoun
V1214 | 21/11/2016 | 24/11/2016 | 35.56 | 25.37
V1214 | 2016-12-02 | 2016-12-06 | 37.5254 | 27.8356
V1214 | 2016-12-10 | 2016-12-14 | 29.486 | 27.247
|  | Avg. | 34.1905 | 26.8175
V1618TA | 25/11/2016 | 28/11/2016 | 42.51 | 25.3
v1898 | 29/11/2016 | 2016-12-01 | 42.02 | 34
v1898 | 2016-07-12 | 2016-12-14 | 41.99 | 33.38
|  | Avg. | 42.1733 | 30.8933

## condensate recovery
2015-16 |  |  |  |  | 2016-17
| MT |  |  |  | MT
Month | condensate recovery |  |  | Month | condensate recovery
2015-04-01 | 190 |  |  | 2016-04-01 | 463
2015-05-01 | 393 |  |  | 2016-05-01 | 489
2015-06-01 | 388 |  |  | 2016-06-01 | 583
2015-07-01 | 404 |  |  | 2016-07-01 | 492.36
2015-08-01 | 341 |  |  | 2016-08-01 | 400
2015-09-01 | 347 |  |  | 2016-09-01 | 424
2015-10-01 | 456 |  |  | 2016-10-01 | 511
2015-11-01 | 381 |  |  | 2016-11-01 | 560
2015-12-01 | 586 |  |  | 2016-12-01 | 800
2016-01-01 | 609 |  |  | 2017-01-01 | 1100
2016-02-01 | 692 |  |  | 2017-02-01 | 783
2016-03-01 | 693 |  |  | 2017-03-01 | 680
Total | 5480 |  |  | Total | 7285.36
[6 empty] | 04.01.2017 | 05.01.2017 | 06.01.2017 | 07.01.2017 | 08.01.2017 | 09.01.2017 | 10.01.2017 | 11.01.2017 | 12.01.2017 | 13.01.2017 | 14.01.17 | 15.01.17 | 16.01.17 | 17.01.17 | 18.01.17 | 19.01.17 | 20.01.17 | 21.01.17 | 22.01.17 | 23.01.17 | 24.01.2017 | 25.01.2017 | 26.01.2017 | 27.01.2017 | 28.01.2017 | 29.01.2017 | 30.01.17 | 31.01.17
[6 empty] | 2280 | 2280 | C1214 | C1214 | C1214 | C1214 | C1214 | C1214 | C1214 | C1214 | C1698 | C1698 | C1698 | C1698 | C1698 | C1618 TA | C1618 TA | C1618 TA | C1618 TA | C1618TA | C1618 50;50 | C1618 50;50 | C1618 50;50 | C1214 | C1214 | C1214 | C1214 | C1214
|  | %tage increase in recovery | 24.7807

## effluent Generation
| Effluent generation 2015-16 | M3/day | Effluent generation 2016-17 | m3/day
APRIL | 1627 | 54.2333 | 1500 | 50
MAY | 1715 | 57.1667 | 1325 | 44.1667
JUNE | 1753 | 58.4333
JULY | 1633 | 54.4333
AUGUST | 1730 | 57.6667 | 1447 | 48.2333
SEPTEMBER | 1733 | 57.7667 | 1377 | 45.9
OCTOBER | 1466 | 48.8667 | 1208 | 40.2667
NOVEMBER | 1788 | 59.6 | 875 | 29.1667
DECEMBER | 1711 | 57.0333 | 884 | 29.4667
JANUARY | 1427 | 47.5667 | 1320 | 44
FEBRUARY | 1242 | 41.4 | 1114 | 37.1333
MARCH | 1447 | 48.2333 | 1164 | 38.8
Total | 19272 | 53.5333 | 12214 | 33.92