## Sheet1
| KRA 1.1 | KRA 1.2 | KRA 1.2 | KRA 1.2 | KRA 1.2 | KRA 1.3 | KRA 1.3 | KRA 1.3 | KRA 1.4 | KRA 1.5 | KRA 1.5 | KRA 1.5
| Sp.Consm. | Efficiency | Efficiency | Efficiency | Efficiency | Efficiency | Efficiency | Efficiency | Temperature | Pressure | Purity | Dew Point | Month | Avg generation per hour (KWH) | SCM/KWH
2016/17 | Gas Turbine | TP-45 A | TP-45-B | TP-45C | Coal Heaters | SM-30 | SM-50 | HRSG | VAM | N2 Plant | N2 Plant | Inst. Air | 2016-04-01 | 5106.925 | 0.324
APRIL | 0.324 | Not Run | Not Run | Not Run | 71 | 84.1216 | 85.6661 | 98.5 | 5.147 | 4.15 | 99.78 | -38.2 | 2016-05-01 | 5280.223 | 0.321
MAY | 0.321 | 90.65 | 90.84 | Not Run | 74 | 86.0586 | 85.5203 | 97.3 | 6.5 | 3.95 | 99.72 | -38.2 | 2016-06-01 | 5200.083 | 0.322
JUNE | 0.322 | Not Run | Not Run | Not Run | 73 | 85.7242 | 86.9649 | 97.7 | 5.466 | 4.23 | 99.76 | -38.2 | 2016-07-01 | 5844.709 | 0.309
JULY | 0.309 | Not Run | Not Run | Not Run | 71 | 86.3965 | 85.751 | 99.4 | 5.73 | 4 | 99.7 | -38.2 | 2016-08-01 | 5309.463 | 0.317
AUG | 0.317 | 90.85 | 90.85 | Not Run | 72.5 | 84.487 | 84.1333 | 98.9 | 5.33 | 3.9 | 99.61 | -38.2 | 2016-09-01 | 5539.268 | 0.312
SEPT | 0.312 | 90.85 | 90.85 | Not Run | 70.8 | 85.6324 | 84.6008 | 94.5 | 5.77 | 3.95 | 99.6443 | -38.2 | 2016-10-01 | 5011.761 | 0.325
OCT | 0.325 | 90.85 | 90.7% | Not Run | 73.5 | 84.9266 | 85.3706 | 95.4 | 6.0901 | 3.5419 | 99.6274 | -38.2 | 2016-11-01 | 5188.941 | 0.323
NOV | 0.323 | Not Run | Not Run | Not Run | 74 | 83.78 | 84.6708 | 94.7 | 5.08 | 3.9966 | 99.7976 | -38.2 | 2016-12-01 | 5615.4 | 0.313
DEC | 0.313 | Not Run | Not Run | Not Run | 71.5 | 84.3137 | 85.751 | 96.6 | 5.62 | 4.4129 | 99.9603 | -38.2 | 2017-01-01 | 5433.002 | 0.317
JAN | 0.317 | Not Run | Not Run | Not Run | 73.8 | 83.85 | 85.751 | 97.8 | 5.57 | 4.2161 | 99.9339 | -38.2 | 2017-02-01 | 5459.514 | 0.32
FEB | 0.32 | Not Run | Not Run | Not Run | 72.6 | 83.65 | 84.6708 | 98.5 | 5.86 | 4.175 | 99.9254 | -38.2 | 2017-03-01 | 5482.807 | 0.317
MAR | 0.317 | Not Run | Not Run | Not Run | 71 | 83.3137 | 85.751 | 98.6 | 5.73 | 4.0226 | 99.8671 | -38.2 | Average | 5372.6747 | 0.31833 | SCM/KWH
Average | 0.31833 | 90.8 | 90.84 | #DIV/0! | 72.3917 | 84.6879 | 85.3835 | 97.1556 | 5.6422 | 4.0239 | 99.7851 | -38.2 |  |  | 318.3333 | SCM/MWH
Target | 321 scm/kwh | 91% | 91% | 91% | 76% | 88% | 88% | 96% | 5 Deg C | 4 Kg/cm2 | 99.5% | (-38 degC) | Target |  | 321 | SCM/MWH
% | 100.5234 | 99.7802 | 99.4176 |  | 99.3367 | 96.6818 | 96.9659 | 100.4792 | 88.6525 | 111.1111 | 100.0804 | 100.5263 |  | NG Cost | Diff | MWH | Rs.
[13 empty] | saving | 26.7 | 2.6667 | 5.372 | 3212885.76