## Paharpur CT
Syndate Plant Vapour Condenser
Paharpur Cooling Tower |  |  | E-104
E-105
GDP
E-106
P-9002 A/B Q= 500 M3/Hr H=45 M P=80 KW | P-20 P03 Q= 435 M3/Hr H=60 M P=110 KW |  | E-114
Precon Condenser
E-115
OLD SPD PHE
Vapour Condenser
Bleacher
Old Postcon (Run only when JST & LST is running)

## Alpha Laval CT
Alpha Laval Cooling Tower
P-364 A/B Q= 300 M3/Hr H=50 M P=75 KW
PHE

## Heat Load of Paharpur (PFAD)
GDP
E-104 | Cooler |  |  | E-114 |  |  |  | E-106 | ATFD Condenser
CW Tin | 36 | °C |  | CW Tin | 36 | °C |  | CW Tin | 36 | °C
CW T out | 39 | °C |  | CW T out | 39 | °C |  | CW T out | 39 | °C
Q | 84.1 | M3/hr |  | Q | 46 | M3/hr |  | Q | 5.7 | M3/hr
Heat Load | 252300 | Kcal/hr |  | Heat Load | 138000 | Kcal/hr |  | Heat Load | 17100 | Kcal/hr
| 83.4325 | TR |  |  | 45.6349 | TR |  |  | 5.6548 | TR
E-105 | Glycerine vapor Condensor |  |  | E-115
CW Tin | 36 | °C |  | CW Tin | 36 | °C
CW T out | 39 | °C |  | CW T out | 39 | °C |  | Total GDP Load | 381.3823 | TR
Q | 233.3333 | M3/hr |  | Q | 15.3 | M3/hr |  | CW flow | 288.325 | M3/hr
Heat Load | 700000 | Kcal/hr |  | Heat Load | 45900 | Kcal/hr
| 231.4815 | TR |  |  | 15.1786 | TR
OLD SPD
CW 4" line is given
[5 empty] | 4" | D | 101.96 | mm | 0.10196 | m
Max flow through 2" line |  | 88.1359 | m3/hr |  |  | A | 0.0081607 | m2
[6 empty] | u | 3 | m/sec | max is considered
delta T assumed |  | 4 | °C |  |  | q | 0.024482 | m3/sec
[7 empty] | 88.1359 | m3/hr
Heat Load |  | 352543.7803 | kcal/hr
|  | 116.5819 | TR
Considering 90% Utilization |  | 104.9237 | TR
| CW flow | 79.3224 | M3/hr
Bleacher Vapour Condenser
CW 2" line is given
[5 empty] | 2" | D | 40.9 | mm | 0.0409 | m
Max flow through 2" line |  | 14.1821 | m3/hr |  |  | A | 0.0013132 | m2
[6 empty] | u | 3 | m/sec | max is considered
delta T assumed |  | 4 | °C |  |  | q | 0.0039395 | m3/sec
[7 empty] | 14.1821 | m3/hr
Heat Load |  | 56728.3327 | kcal/hr
|  | 18.7594 | TR
Considering 80% Utilization |  | 15.0075 | TR
| CW flow | 11.3457 | M3/hr
Syndet Plant Vapour Condenser
CW 2" line is given
[5 empty] | 2" | D | 40.9 | mm | 0.0409 | m
Max flow through 2" line |  | 14.1821 | m3/hr |  |  | A | 0.0013132 | m2
[6 empty] | u | 3 | m/sec | max is considered
delta T assumed |  | 4 | °C |  |  | q | 0.0039395 | m3/sec
[7 empty] | 14.1821 | m3/hr
Heat Load |  | 56728.3327 | kcal/hr
|  | 18.7594 | TR
Considering 70% Utilization |  | 13.1316 | TR
| CW flow | 9.9275 | M3/hr
Precon Vapour Condenser
Note: | Feed rate of Precon when only LST is running & JST is shutdown
LST FEED |  | 10 | TPH
Precon feed rate |  | 6.5 | TPH
Initial Conc |  | 2 | %
Final Conc |  | 8 | %
precon outlet rate |  | 1.625 | TPH
Total vapour load |  | 4.875 | TPH
Water removed from each effect |  | 1.625 | TPH
Heat Load on last effect |  | 877500 | kcal/hr
|  | 290.1786 | TR
| CW flow | 219.375 | M3/hr
TOTAL CW FLOW |  | 608.2955 | M3/hr

## Heat Load of Paharpur (CNO RMO)
GDP
E-104 | Cooler |  |  | E-114 |  |  |  | E-106 | ATFD Condenser
CW Tin | 36 | °C |  | CW Tin | 36 | °C |  | CW Tin | 36 | °C
CW T out | 39 | °C |  | CW T out | 39 | °C |  | CW T out | 39 | °C
Q | 84.1 | M3/hr |  | Q | 46 | M3/hr |  | Q | 5.7 | M3/hr
Heat Load | 252300 | Kcal/hr |  | Heat Load | 138000 | Kcal/hr |  | Heat Load | 17100 | Kcal/hr
| 83.4325 | TR |  |  | 45.6349 | TR |  |  | 5.6548 | TR
E-105 | Glycerine vapor Condensor |  |  | E-115
CW Tin | 36 | °C |  | CW Tin | 36 | °C
CW T out | 39 | °C |  | CW T out | 39 | °C |  | Total GDP Load | 381.3823 | TR
Q | 233.3333 | M3/hr |  | Q | 15.3 | M3/hr |  | CW flow | 288.325 | M3/hr
Heat Load | 700000 | Kcal/hr |  | Heat Load | 45900 | Kcal/hr
| 231.4815 | TR |  |  | 15.1786 | TR
OLD SPD
CW 4" line is given
[5 empty] | 4" | D | 101.96 | mm | 0.10196 | m
Max flow through 2" line |  | 88.1359 | m3/hr |  |  | A | 0.0081607 | m2
[6 empty] | u | 3 | m/sec | max is considered
delta T assumed |  | 4 | °C |  |  | q | 0.024482 | m3/sec
[7 empty] | 88.1359 | m3/hr
Heat Load |  | 352543.7803 | kcal/hr
|  | 116.5819 | TR
Considering 90% Utilization |  | 104.9237 | TR
| CW flow | 79.3224 | M3/hr
Bleacher Vapour Condenser
CW 2" line is given
[5 empty] | 2" | D | 40.9 | mm | 0.0409 | m
Max flow through 2" line |  | 14.1821 | m3/hr |  |  | A | 0.0013132 | m2
[6 empty] | u | 3 | m/sec | max is considered
delta T assumed |  | 4 | °C |  |  | q | 0.0039395 | m3/sec
[7 empty] | 14.1821 | m3/hr
Heat Load |  | 56728.3327 | kcal/hr
|  | 18.7594 | TR
Considering 80% Utilization |  | 15.0075 | TR
| CW flow | 11.3457 | M3/hr
Syndet Plant Vapour Condenser
CW 2" line is given
[5 empty] | 2" | D | 40.9 | mm | 0.0409 | m
Max flow through 2" line |  | 14.1821 | m3/hr |  |  | A | 0.0013132 | m2
[6 empty] | u | 3 | m/sec | max is considered
delta T assumed |  | 4 | °C |  |  | q | 0.0039395 | m3/sec
[7 empty] | 14.1821 | m3/hr
Heat Load |  | 56728.3327 | kcal/hr
|  | 18.7594 | TR
Considering 70% Utilization |  | 13.1316 | TR
| CW flow | 9.9275 | M3/hr
Precon Vapour Condenser
Note: | Feed rate of Precon when only LST is running & JST is shutdown
LST FEED |  | 10 | TPH
Precon feed rate |  | 7.7 | TPH
Initial Conc |  | 15 | %
Final Conc |  | 30 | %
precon outlet rate |  | 3.85 | TPH
Total vapour load |  | 3.85 | TPH
Water removed from each effect |  | 1.2833 | TPH
Heat Load on last effect |  | 693000 | kcal/hr
|  | 229.1667 | TR
| CW flow | 173.25 | M3/hr

## Heat Load of Alphalaval
Postcon Vapour Condenser
Note: | Feed rate of Postcon when only LST is running & JST is shutdown
Considering PFAD Run
LST FEED |  | 10 | TPH
Postcon feed rate |  | 5 | TPH
Initial Conc |  | 9 | %
Final Conc |  | 87 | %
precon outlet rate |  | 0.51724 | TPH
Total water removed |  | 4.4828 | TPH
Water removed from each effect |  | 1.4943 | TPH
Heat Load on last effect |  | 806896.5517 | kcal/hr
|  | 266.8309 | TR
| CW flow | 201.7241 | M3/hr
Considering RMO/CNO Run
LST FEED |  | 10 | TPH
Postcon feed rate |  | 5 | TPH
Initial Conc |  | 30 | %
Final Conc |  | 89 | %
precon outlet rate |  | 1.6854 | TPH
Total water removed |  | 3.3146 | TPH
Water removed from each effect |  | 1.1049 | TPH
Heat Load on last effect |  | 596629.2135 | kcal/hr
|  | 197.298 | TR
| CW flow | 149.1573 | M3/hr

## Summary
Summary
PAHARPUR COOLING TOWER
| ACTUAL | PFAD RUN | CNO /RMO RUN
Consumer | Heat Load | If GDP & LST on 80% load | Heat Load
TR
GDP | 381.3823 | 305.1058 | 381.3823
OLD SPD | 104.9237 | 0 | 0
MCT BLEACHER | 15.0075 | 15.0075 | 15.0075
Syndate | 13.1316 | 13.1316 | 13.1316
Precon | 290.1786 | 232.1429 | 229.1667
Total | 804.6236 | 565.3877 | 638.688
Alphalaval Cooling Tower
| ACTUAL | PFAD RUN | CNO /RMO RUN
Consumer | Heat Load | If GDP & LST on 80% load | Heat Load
Pastcon Load | 266.8309 | 213.4647 | 197.298
Total Load | TR | 778.8524 | 835.986
Pharpur CT capacity | TR | 860
Note : If Old SPD is not running & GDP & LST are at 80% loading (Considering PFAD Run) then Paharpur cooling tower can cater the Alpha laval Cooling tower load
Note : If Old SPD is not running & GDP (Considering CNO/RMO Run) then Paharpur cooling tower can cater the Alpha laval Cooling tower load

## Actual saving
Pump calculated power
Name of equipment | P20P03 | P9002A | P9002B | P 364 | Pharpur CT fan | Alpha Laval CT fan
calculated power | 135.8742 | 79.6717 | 80.2893 | 71.6428 | 28 | 18.5
127.2277
Month | 2016-11-01 | 2016-12-01 | 2017-01-01 | 2017-02-01 | 2017-03-01
Power Cost Rs/KWH | 5.66 | 6.18 | 6.06 | 5.99 | 5.9
Date | Working Hrs |  |  | Plants Running |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  |  |  | GDP | Alfalaval
2016-11-22 | 8 |  |  | Stopped | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.019283
2016-11-23 | 24 |  |  | Stopped | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.05785
2016-11-24 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-25 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-26 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-27 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-28 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12245
2016-11-29 | 24 |  |  | Stopped | on | P20P03 & P364 | Paharpur CT & Alfalaval
2016-11-30 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.046104
0.73549
Date | Working Hrs |  |  | Plants Running |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  |  |  | GDP | Alfalaval
2016-12-01 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-02 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-03 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-04 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-05 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-06 | 24 |  |  | on | on | P20P03 & P9002A & B | Paharpur CT | 315.1886 | 334.3063 | 19.1176 | 0.028355
2016-12-07 | 24 |  |  | on | on | P20P03 & P9002A & B | Paharpur CT | 315.1886 | 334.3063 | 19.1176 | 0.028355
2016-12-08 | 24 |  |  | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014615
2016-12-09 | 24 |  |  | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014615
2016-12-10 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-11 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-12 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-13 | 24 |  |  | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-14 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-15 | 24 |  |  | Stopped | on | P9002A | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-16 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-17 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-18 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-19 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-20 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-21 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-22 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-23 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-24 | 24 |  |  | on | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13278
2016-12-25 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-26 | 24 |  |  | on | on | P20P03 & P9002B | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.05034
2016-12-27 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-28 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-29 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-30 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2016-12-31 | 24 |  |  | on | on | P20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.063165
2.581
Date | Working Hrs | Plants Running |  |  |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  | JST | LST | GDP | Alfalaval
2017-01-01 | 24 | on | on | on | on | 20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.061938
2017-01-02 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-03 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-04 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-05 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.1311
2017-01-06 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-07 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-08 | 24 | Stopped | on | on | on | 20P03 | Paharpur CT | 155.2277 | 197.8145 | 42.5868 | 0.061938
2017-01-09 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-10 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-11 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-12 | 24 | on | on | on | on | P9002B & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-13 | 24 | on | on | on | on | P9002B & 20P03 | Paharpur CT | 244.1635 | 278.1037 | 33.9403 | 0.049363
2017-01-14 | 24 | on | on | on | on | P9002A & B &20P03 | Paharpur CT | 315.1886 | 334.3063 | 19.1176 | 0.027805
2017-01-15 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.13021
2017-01-16 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-17 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-18 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-19 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-20 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-21 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-22 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-23 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-24 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-25 | 24 | Stopped | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-26 | 24 | Stopped | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-27 | 24 | on | on | Stopped | on | P9002A & B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014331
2017-01-28 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
2017-01-29 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
2017-01-30 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
2017-01-31 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.050261
1.5249
Date | Working Hrs | Plants Running |  |  |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  | JST | LST | GDP | Alfalaval
2017-02-01 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-02 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-03 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-04 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-05 | 24 | Stopped | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-06 | 24 | Stopped | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-07 | 24 | Stopped | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-08 | 24 | on | on | on | Stopped | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-09 | 24 | on | on | on | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12959
2017-02-10 | 24 | on | on | on | on | P9002A& B | Paharpur CT | 187.961 | 197.8145 | 9.8535 | 0.014165
2017-02-11 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-12 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-13 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-14 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-15 | 24 | on | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-16 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-17 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-18 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-19 | 24 | Stopped | on | Stopped | on | P9002B | Paharpur CT | 108.2893 | 197.8145 | 89.5252 | 0.1287
2017-02-20 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-21 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-22 | 24 | on | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-23 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-24 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-25 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-26 | 24 | Stopped | on | on | on | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-27 | 24 | Stopped | on | on | Stopped | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2017-02-28 | 24 | Stopped | on | on | Stopped | P9002A & 20P03 | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.04968
2.4663
Date | Working Hrs | Plants Running |  |  |  | Pump Running | CT Running | Power consumption after modification | Power consumption before modification | Power saving (KWH) | Actual Saving (Lacs)
|  | JST | LST | GDP | Alfalaval
2017-03-01 | 24 | Stopped | on | on | Stopped | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-02 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-03 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-04 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-05 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-06 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-07 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-08 | 24 | Stopped | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-09 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-10 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-11 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-12 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-13 | 24 | on | on | Stopped | on | P9002A | Paharpur CT | 107.6717 | 197.8145 | 90.1428 | 0.12764
2017-03-14 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-15 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-16 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-17 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-18 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-19 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-20 | 24 | on | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-21 | 24 | Stopped | Stopped | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-22 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-23 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-24 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-25 | 24 | on | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-26 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-27 | 24 | Stopped | on | on | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-28 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-29 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-30 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2017-03-31 | 24 | on | on | Stopped | on | 20P03 & P9002A | Paharpur CT | 243.5459 | 278.1037 | 34.5579 | 0.048934
2.1466
Note on C6: Author: If running with another pump
Note on C7: Author: If running single

## Estimated Saving
Saving in Power consumption
Alphalaval Cooling Tower FAN Power | 18.5 | KWH
loading 90% | 16.65 | KWH
Alpha laval CT circulation pump | 75 | KWH
loading 70% | 52.5 | KWH
Total power saving | 69.15 | Kwh
Working days | 80 | Days
Power Cost | 5 | Rs/kwh
Saving | 663840 | Rs
| 6.6384 | Lacs
Saving in raw water consumption
CT water circulation rate | 240 | m3/hr
Drift losses avoided | 0.048 | m3/hr
Raw water saving | 92.16 | M3
Saving | 3317.76 | Rs
| 0.033178 | Lacs
Total Saving | Lacs | 6.6716
Total Investment | Lacs | 1.1821
ROI | Months | 2.1263

## Costing
Material Cost
Sr.no. | Description | Quantity | Unit | Rate | Amount (Rs.) | Available quantity | Unit | Amount based on material availability (Rs.)
1 | PIPE CS-ASTMA106GRB 10" ERW SCH40 | 18 | M | 2600 | 46800 | 18 | M | 0
2 | FLANGE, CS, 150#, 10" | 2 | Nos | 2250 | 4500 | 2 | Nos | 0
3 | Elbow CS, Sch 40,ERW,90 D | 6 | Nos | 1300 | 7800 | 6 | Nos | 0
4 | Tee,CS,10x10 ,Sch 40 | 2 | Nos | 2200 | 4400 | 0 | Nos | 4400
5 | Valve, Butterfly, 10", CS, 150#, FE | 1 | Nos | 16000 | 16000 | 0 | Nos | 16000
7 | Gasket ,CAF,150# | 2 | Nos | 42 | 84 | 2 | Nos | 0
8 | Nut bolts & other | 1 | Lot | 5000 | 5000 | 0 | Lot | 5000
| Total | [6 empty] | 25400
| Taxes ( 14.5 %) | [6 empty] | 3683
| Total (Including taxes) | [6 empty] | 29083
Service cost
Sr.no. | Description | Quantity | Unit | Rate | Amount (Rs)
1 | CS pipe line fabrication weld joint | 60 | IND | 126 | 7560
2 | CS Pipe erection and fabrication | 180 | INM | 210 | 37800
3 | Hydra Or Material handling | 1 | SHF | 8925 | 8925
4 | Valve Fixing | 10 | IND | 126 | 1260
5 | DP test | 180 | IND | 32 | 5760
6 | Scaffolding | 1 | LOT | 10000 | 10000
| Total |  |  |  | 71305
| Taxes ( 25 %) |  |  |  | 17826.25
| Total (Including taxes) |  |  |  | 89131.25
Total cost |  |  |  |  | 118214.25

## Sheet1
Summary
PAHARPUR COOLING TOWER
| ACTUAL | PFAD RUN | CNO /RMO RUN
Consumer | Heat Load | If GDP & LST on 80% load | Heat Load
| TR | TR | TR
GDP | 381.3823 | 305.1058 | 381.3823
OLD SPD | 104.9237 | 0 | 0
MCT BLEACHER | 15.0075 | 15.0075 | 15.0075
Syndate | 13.1316 | 13.1316 | 13.1316
Precon | 290.1786 | 232.1429 | 229.1667
Total | 804.6236 | 565.3877 | 638.688
ALPHALAVAL COOLING TOWER
| ACTUAL | PFAD RUN | CNO /RMO RUN
Consumer | Heat Load | If GDP & LST on 80% load | Heat Load
| TR | TR | TR
Pastcon Load | 266.8309 | 213.4647 | 197.298
Total Load | TR | 778.8524 | 835.986
Pharpur CT capacity | TR | 860
Note : If Old SPD is not running & GDP & LST are at 80% loading (Considering PFAD Run) then Paharpur cooling tower can cater the Alpha laval Cooling tower load
Note : If Old SPD is not running & GDP (Considering CNO/RMO Run) then Paharpur cooling tower can cater the Alpha laval Cooling tower load