1) C-303:==FT-R351A & FT-R351B are integral mounting ,they getting heating problem due to that it showing wrong indication & also chance of sensor failure .they convert integral to remote dated on 26 oct 2016.Now they working okay. 2)SPD-FT-50519A showing wrong indication & also chance of sensor failure .they convert integral to remote dated on 13 july 2017 3)C-402 FT-4305 -vortex shedding frequency changed ,now working okay. 4)Fatty Alcohol FT-1003 New high temp sensor replaced with spare on dated on 16 nov 2016 5) Fatty Acid XV-9504 Spare control valve prepared for installation, fabrication drawing submitted to mechanical dept 6)Column attached TT in DFA section & H2 caloric == damaged sensor & thermowell replaced with spare one (TT-3203,TT-3207,TT-3205,TT-4311,TT-106,TT-113,TT-104,TT-109,TT-10010,TT-10011,TT-10006,TT-353)